## Slide 1: Laminar Tube Flocculator
Victoria Chou and Yining Dai
Fall 2013

## Slide 2: Outline
Introduction
Floc Breakup Theory
Base Case Testing
Experiments
Challenges Faced

## Slide 3: Introduction
Flocculation is an integral part of the water treatment process

## Slide 4: Floc Breakup
“Large flocs are useless”
  Shear is too large, so colloids cannot attach
Use clamps to break up flocs so that they can regrow and collect more colloids as they travel

## Slide 5: Set Up of Fall 2013 Testing
Notes: Allow more time for the flocs to grow
Previously the two turbidimeters did not agree with each other
Also they wanted to test tygon tubes vs. silicon tubes (Spring 2013)

## Slide 6: Experiment- Process Controller
1. Backwash entire
2. Loading
3. Pump ramp down
4. Closing of ball valve
5. Settling
6. Reopening of ball valve
Operational States
Notes: Stage 1-3 Yining
Stage 4-6 Vicki

## Slide 7: Base Case Testing
Base Case Testing
  Linear dosing
  Power law dosing
  Dose=coefficient x base
  coefficient = .25
  base = 1.25
  max reps = 12
max reps

## Slide 8: Base Case One

## Slide 9: Base Case Two

## Slide 10: Base Case Three
Notes: 10/11

## Slide 11: 1st Experiment- Clamp Size
Testing the Effectiveness of Different Sized Clamps
Have ONE clamp on the middle arrangement of tubing
4 mm & 5 mm
Have dosages of 0 to 3 mg/L PACl
4mm
5mm

## Slide 12: Results of Summer 2013 Research
Notes: Used results from summer to choose the clamp sizes (4mm-5mm)

## Slide 13: Preliminary Results
Notes: One 4mm clamp
-has higher residual turbidity than with no clamps
-suggesting that floc breakup may not help

## Slide 14: Preliminary Results
Notes: One 4mm clamp
-has higher residual turbidity than with no clamps
-suggesting that floc breakup may not help

## Slide 15: 2nd Experiment- Clamp Number
Testing the Effectiveness of Different Number of Clamps
1-16 clamps spread evenly across the middle arrangement of tubing

## Slide 16: Challenges Faced
Residual coagulant on tubing
  “Pigging”
Turbidimeters
  Clean the glass column
  Clean the vial
  Calibration
Pump malfunction
Pinch valve
  Keep it unclogged by washing periodically
Algae growth in the tubing
  Replaced with clean tubing

## Slide 17: Questions?