## Slide 1: Laminar Tube Flocculator
Victoria Chou and Yining Dai
Fall 2013

## Slide 2: Outline
Introduction
Floc Breakup Theory
Base Case Testing
Experiments
Conclusions from our research
Challenges Faced
Future Work

## Slide 3: Introduction
Flocculation is an integral part of the water treatment process

## Slide 4: Floc Breakup Theory
“Large flocs are useless”
  Shear is too large, so colloids cannot attach
Use clamps to break up flocs so that they can regrow and collect more colloids as they travel

## Slide 5: Set Up of Fall 2013 Testing
Notes: Allow more time for the flocs to grow
Previously the two turbidimeters did not agree with each other
Also they wanted to test tygon tubes vs. silicon tubes (Spring 2013)

## Slide 6: Set Up of Fall 2013 Testing
Length of tubing

## Slide 7: Set Up of Fall 2013 Testing
Material used for Tubing

## Slide 8: Base Case Testing
Base Case Testing
  Linear dosing
  Power law dosing
  Dose=coefficient x base
  coefficient = .25
  base = 1.25
  max reps = 12
max reps

## Slide 9: Base Case Results

## Slide 10: 1st Experiment- Clamp Size
Testing the Effectiveness of Different Sized Clamps
Have ONE clamp on the middle arrangement of tubing
4 mm & 5 mm
Have dosages of 0 to 2 mg/L PACl
4mm
5mm

## Slide 11: Results of Summer 2013 End Clamp Research
Notes: Used results from summer to choose the clamp sizes (4mm-5mm) – end clamp testing

## Slide 12: Results of Clamp Testing

## Slide 13: Statistical Testing
Used a t-test to test for a significant difference between two sets of data
  Compared base case to 4 mm
  Dosage of 0.8 mg/L
  p-value = 0.008
  Dosage of 1.8 mg/L
  p-value = 0.036

## Slide 14: Statistical Testing cont.
  Compared base case to 5 mm
  Dosage of 0.8 mg/L
  p-value = 0.934
  Dosage of 1.8 mg/L
  p-value = 0.177

## Slide 15: Conclusions Drawn
4 mm clamp significantly increases residual turbidity
5 mm clamp – graphs vs. statistical testing
More trials of the 5 mm clamp
Experiment with 6 and 7 mm clamps

## Slide 16
Fig. 4 Residual turbidities before and after ﬂocs breakage and re-formation in model water II.
Wenzheng Yu , Guibai Li , Yongpeng Xu , Xue Yang
Breakage and re-growth of flocs formed by alum and PACl
Powder Technology Volume 189, Issue 3 2009 439 – 443
http://dx.doi.org/10.1016/j.powtec.2008.07.008
Literature

## Slide 17: Future Work
Testing the Effectiveness of Different Number of Clamps
1-16 clamps spread evenly across the middle arrangement of tubing
Tapered Flocculator
Increase the tube diameter to decrease the energy dissipation rate

## Slide 18: Challenges Faced
Pump malfunction
  Centrifugal pump
Pressure Sensors
  The t-connectors are facing upwards

## Slide 19: Questions?