## Slide 1: Tube Flocculator
Patience Ruijia Li

## Slide 2: Outline
Introduction
Tasks
Materials & Methods
Apparatus
Experiments

## Slide 3: Introduction
Floc formation for removal in sed tank

## Slide 4: Introduction
Goal
-- To develop flocculation models in laminar flow
-- To determine the parameters that affect flocculation to minimize residual turbidity
Application for AguaClara
-- Guide flocculation design

## Slide 5: Tasks
Previous work
--- Minimum alum dose needed to induce flocculation (various influent turbidity)
--- Length of flocculator (HRT)
--- Capture Velocity
--- Optimal dosage of PACl and Na2CO3 (pH)
--- Ionic strength of raw water
( I ↓, coagulation↓, residual turbidity ↑ )
Other parameters that matter?
energy dissipation rate

## Slide 6: Tasks
Standard curve of turbidity versus dose.
Measure residual turbidity over a range of chemical doses (capture velocity).
Measure residual turbidity under the same experimental conditions but with breakup of large flocs at regular intervals.

## Slide 7: Coiled Tube Flocculation Residual Turbidity Analyzer
Dr. Karen Swetland Dissertation research
Notes: Here we plotted the residual turbidity, the turbidity of the water after settling, against the coagulant dose. We noticed that when we used a log-log plot, there was a linear trend in the data. So we explored further.

## Slide 8: Data is consistent with the hypothesis that large flocs are useless
PACl
Alum
Capture velocity: 0.12 mm/s
244,000 data points
Notes: These are the results! For a capture velocity of 0.12 mm/s the data collapses to a line with an R^2 around 0.9 for both. Keep in mind that this graph encompasses 244,000 data points…
k = 0.7

## Slide 9: Materials
Clay water: 10 g/L clay solution
Alum water: 2.5 g/L
Raw water: from the tap
3 pumps, several tubes, valves…
Detailed material list can be found at
https://confluence.cornell.edu/display/AGUACLARA/FReTA+Apparatus+Materials+List

## Slide 10: Methods: Apparatus
Synthetic raw water (SRW) and coagulant metering system
Rapid mix
Tube flocculator
Flocculation residual turbidity analyzer (FReTA)
All Managed by
Process Controller

## Slide 11: Methods: floc breakup
How to break large flocs?
-- Floc size?
Based on energy dissipation rate:
Dorifice = 6.093 mm
Dtubeflocculator = 9.525 mm

## Slide 12: Experiments
1. Backwash entire
2. Loading
3. Pump ramp down
4. Closing of ball valve
5. Settling
6. Reopening of ball valve
Operational States