# AguaClara: Gravity powered chemical dose controller system for aluminum sulfate and chlorine dosing

## Abstract	 (Do this next so you know what you want to include)

## For LFOM:

A non-electrical technique for the regulation of chemical dose in water treatment plants was tested at pilot scale and then implemented in a full scale water treatment. A Linear Flow Orifice Meter (LFOM) based on the concept of the Sutro weir was added to the entrance tank of the water treatment plant. The LFOM was evaluated for linearity and flow measurement accuracy over a range of flows from 20 to 140 L/min. The flow rate was shown to be linearly related to water height. The linear response of the LFOM was coupled with the linear output of a flow controller to create the chemical dose controller. This innovation eliminates the need for plant operators to adjust the chemical feed when the flow rate through the plant changes.

## Introduction

Adaptation of conventional drinking water treatment technologies for use in the Global South is a concern of growing urgency. Conventional water treatment technologies that have been imported into the Global South frequently fail and are abandoned for three reasons.

- Conventional technologies rely on customized components that are not available in the Global South

- The reliance on electricity to power pumps, mixers, and valves results in excessively high operating costs

- Conventional technologies are often not designed to facilitate operator monitoring and regulation of the flocculation process. For example the control panel for the plant is inside an office building and the flocculation process is out in the open and far from the control panel.

The lack of clean drinking water provides avenues for infection by waterborne pathogens which are currently one of the major causes of mortality for children under five years old. The AguaClara team is working to bring clean water to communities with a flocculation-sedimentation water treatment design. The design requires the addition of aluminum sulfate (alum) as a coagulation agent. Plant operators manually adjust the alum dose based on the daily flow rate of the treatment facility. In the first AguaClara plants that were constructed, the dosage of aluminum sulfate and chlorine by the operators was imprecise. There was no specific system to allow the operator for the AguaClara plants to accurately dose the alum and chlorine as the turbidity or through the plant changed. Therefore, it became absolutely necessary to implement a chemical dosing system that would allow the AguaClara plant operators to accurately dose chemicals based on the conditions throughout the plant. In the first AguaClara plants the operator adjusted the chemical flow rate and thus indirectly controlled the dose. Plant operators would manually adjust the chemical flow rate based on the incoming turbidity.

A useful innovation is necessary in the regulation of aluminum hydroxide into the system as the flow changes without the use of electrical devices. Currently options for the control of chemical additions to water treatment plants are either an electric pump or manual adjustment of chemical flows. The AguaClara plant operators would set the alum dose in the initial AguaClara plants. However, the operators would become accustomed to setting a flow rate for the dosage of chemical, but lose the connection with coagulant concentration.

Computer controlled water treatment plants are not robust or sustainable in the Global South because of the lack of a reliable supply chain for specialized components and because of frequent power outages and surges. Five gravitationally powered plants researched and designed by AguaClara are currently operational in Honduras, but chemical dosing without electric pumps is still inconsistent at the plants. Alum (aluminum sulfate) dosing must be adjusted regularly because it depends on the influent turbidity, a function of season and rainfall. Chlorine dosing must be consistent, and both chlorine and alum doses must be easily controlled. Here we describe the research and development of an effective flow controller that can tie into AguaClara systems between the alum stock tank and the flocculator inlet at the rapid mix and between the chlorine stock tank and the system. The flow controller dampens the effect of the chemical level changes in the stock tanks, using a simple manufactured float valve to maintain a near-constant chemical level in the flow controller, which acts as a constant head tank. The height at which the outflow tubing from the flow controller connects to the system can be adjusted to change dosing flow. The flow controller is both inexpensive to produce and simple to operate.

Objectives

Chemical Dose Controller

- Easily adapted for a range of flow rates

- Completely gravity powered

- Open source so that anyone can build it and use it

## Flow Controller

Calibrated to easily vary the flow rate.

- Maintain a constant flow rate independent of the chemical level in the stock tank

- Handle corrosive chemicals

- Incorporate a linear scale to facilitate setting the flow

- without need to use trial and error

- Resistant to clogging

- Easy to maintain and operate

- Economical, small and easily used to replace existing

- flow control devices

Linear Flow Orifice Meter (LFOM)

- Regulate the flow of alum into the rapid mixer according to changes in flow rate.

- Keep alum dose as close to constant as possible.

- Be able to install device into existing plants.

- Include a simple way for the plant operator to change the dosage.

Chemical Doser

- Must be flexible.

- Automatically adjust the head loss in the chemical dosing system in response to plant inflow changes

## Theory

### Overall Design

The chemical dose controller is currently comprised of three components, the linear flow orifice meter, the flow controller, and a chemical doser (Figure 1). These components of the system act together to allow the plant to respond to changes in inflow by both linearizing the change in plant flow and automatically adjusting chemical dosing to the plant. With this system AguaClara plants should be more resilient because operators are only required to adjust chemical dosing settings based on incoming turbidity, not based on flow rates.

Figure 1: Overall design schematic of chemical dose controller

### Linear Flow Orifice Meter (LFOM)

The purpose of our project is to design a mechanism to regulate the flow of alum into the rapid mixer according to changes in flow rate. Currently the existing plants require manual adjustment of the alum flow rate when the plant flow gets too high or too low. Correct alum dose is very important to the performance of the flocculation and sedimentation processes, and as it exists the job of keeping a constant alum dose is left open to human error. Automation of this process would improve the performance and efficiency of the plant and simplify the operator's responsibilities. The Linear Flow Orifice Meter would need to meet the goals stated earlier.

Regarding the overall goals of the Chemical Dose Controller, all the goals of its separate components will need to be integrated along with the goals for their combined use. First, the Chemical Dose Controller will need to

maintain the alum dose as close to constant as possible. Second, the system must be able to be installed and integrated into existing AugaClara plants easily.

Finally,

the Chemical Dose Controller needs to include a simple way for the plant operator to change the dosage.

During the design of the overall Chemical Dose Controller, various questions arose that guided the direction of the design of the regulated alum flow system. The design will be based around the plant operator taking a relative measurement of the plant flow rate and using that to regulate the alum flow into the rapid mixer.  Then, this information will need to be transferred automatically using simple and non-electronic methods. In addition, this system will need be an efficent method to accurately regulate the alum flow without the use of valves or pumps.

The method used to keep track of the plant flow rate is a measurement of the water level in the grit chamber. This showed itself to be a major complicating factor, as the head in a tank and the flow rate into that tank are not linearly related. The main equation used to model this is the orifice equation:

The equation shows how flow rate is related to the square root of the change in head.

### Chemical Doser (CD)

The design for the chemical doser proposed uses an entrance tank as a way to transfer information about the flow rate to the aluminum hydroxide flow control module through a float system. The system accurately delivers consistent aluminum hydroxide dosing into the incoming water based on the height of the water in the entrance tank. Without intervention the flow rate through the entrance tank is proportional to the square root of the pressure head, height of the water in the entrance tank, as shown in equation 1.

Insert orifice Equation

This research is focused on designing an automated chemical doser that can automatically adjust the head loss in the chemical dosing system in response to plant inflow changes. Currently plant chemical dosing is determined based on plant inflow and turbidity. The chemical doser (CD) will eliminate the need for plant operators to dose for inflow, reducing the number of variables and therefore opportunities for error.

One main reason for the focus on this doser is that it will allow plants to be more flexible. Plant inflow is largely variable with weather, both seasonally and hourly. For instance, if there is a high frequency of late night rain storms, then there will be an increase in plant inflow. Ideally the automated chemical dosing system will allow plants to respond to these weather-driven changes without an operator's presence.

## Design

### Linear Flow Orifice Meter

Because flow into the grit chamber is proportional to the square root of head, there is a non-linear relationship between head and flow rate must be accounted for in this design as well. The relationship between water height and flow rate create a problem when transferring of data to other mechanisms. A predictable linear relationship between the height of the water in the entrance tank and the flow rate through the plant allows for a system of floats to meter the aluminum hydroxide flow rate.

#### Sutro Weir Analog Theory

The Sutro weir developed by Victor Sutro in 1915 can be used to create a linear correlation between head and flow rate. In order to account for the non-linear relationship between head and flow rate, a Sutro weir was designed to create a linear relationship between head in a tank and flow rate into the grit chamber. The configuration is shown below in Figure 1.

Figure 1: Linear Weir (Image: Cussons Technology)

Figure 2: Sutro Weir along with equations for its design

The bottom width of the Sutro weir is relatively large and the width gradually decreases as the height increases. As the height of the water in the tank increases the pressure created by the weight of the fluid causes the flow rate through the bottom of the weir to increase. By minimizing the weir width as height increases the change in the total flow through the weir as height increases is kept in a linear relationship. Therefore, we are approximating the Sutro weir analog with a riser pipe added onto the pipes that connect the entrance tank and the flocculation tank. For AguaClara plants, Sutro Weirs are impractical because they are relatively difficult to fabricate and construct on the project sites. Therefore, the LFOM, a Sutro Weir analog, is simpler to construct because it involves only drilling a series of holes.

Using this shape, we decided to construct our own analog using a series of orifices drilled into the grit chamber outlet pipe (Figure 2). The pipe would be easily introduced into previously constructed plants and new plants at low cost. Holes would be drilled into the riser pipe that would mimic the Sutro weir basics of design. The drilling of holes as specified heights doesn't require skilled labor. The water is forced to flow through the riser pipe in order to leave the entrance tank and enter the flocculation tank. Experimental tests were conducted to evaluate the accuracy of the simulated Sutro weir in a pilot plant application.

### Chemical Doser

The chemical doser  has three principle components: a float, a lever arm, and a dosing ring.

The float currently used in the lab for data collection is a 45.5 cm long 10 cm (4 in) PVC tube capped at both ends and partially filled with sand so that it weighs 8 lbs. It rests 33.5 cm below and 12 cm above the water line in a virtual grit chamber, which is a deep bucket with a pressure sensor at its base. This pressure sensor provides readings of the water level in the bucket. The float is connected via low-elasticity fishing line to the lever arm. The lever arm is a 68 cm length of 1 1/4 in schedule 40 PVC pipe with a pivot point at 34 cm (the center). Opposite of the pivot there are notches cut into the pipe at 5 cm length intervals. The chemical doser hangs from these notches.

The chemical dosing tube is a tube with an open T connection at the top, which allows the FC outflow tubing to drain through a pressure break T.  The tubing exiting the pressure break T has a larger diameter than the tubing entering it.  The pressure break and larger outflow tubing allow a free surface at the same height as the discharge to the rapid mix (minus head loss) to form inside the larger tube while air can also flow through the tube.

## Materials and Methods

### Linear Flow Orifice Meter (LFOM)

For our program, the user selects whether a metric or English series of drill bits will be used to make the orifices, thereby giving the area of each orifice. The program sets the flow rate through the first row of holes when the head is one orifice spacing above the holes.

Figure 3: Illustration of flow rate through the first row of holes when the head is one orifice spacing above the holes

This is done by dividing the given maximum plant flow by the desired number of orifice rows. The orifice equation can be used to find the number of orifices needed in this first row. We now have the total orifice area of the first row, allowing us to do a check to see if the given drill bit is too large or too small. We define too large as a diameter larger than our given orifice row spacing. An orifice diameter that is too small creates a situation where more than half the circumference of the pipe is taken up by holes, and we do not want to significantly weaken this pipe. If the bit size is increased, the number of holes would decrease.

The next element of the program is a function which gives the flow rate at any grit chamber head. This then allows us to find the number of orifices in each row which would generate our linear goal. For example, if flow through the first row is 10 L/min, then flow through the first two rows should be 20 L/min, and so on. The program finds the number of holes by first calculating Q for all of the rows of orifices below the current level. If the total calculated flow is less than the desired flow, it adds a tenth of a hole. Once the linear goal is met, the number is rounded to the nearest whole number of orifices, and this repeats for each row of orifices. We can now find the expected flow out of the grit chamber using these orifice sizes, spacing, and numbers, but only when the head is exactly at the height of each row. Our last step, therefore, is to calculate the flow rate for intermediate heads.

### Chemical Doser

The top of the pipe is cut in a saddle shape to fit the lever arm through it and create the pivot.  The height of this base pipe depends on the design constraints of the plant it will be built for.

The FC should be attached to the base pipe with two clamps that are interconnected so that they firmly anchor the FC at the appropriate height for [zeroing the CD|CD Calibration].  Only one clamp was used during experimental testing because the FC was being continually checked and re-zeroed, and it was being used in a very controlled environment.  Additional clamps would be necessary for a robust design.

Currently ¼ inch outer diameter tubing is used to connect the flow controller to the pressure break T, but it is not known what size tubing is necessary to allow air to flow after the T.  Experience has indicated that ½ inch outer diameter tubing is large enough, but it is possible that tubing with an outer diameter as small as 3/8 inch could work as well.  The larger tube is then connected to 1/4 in outer diameter tubing, which connects the CD to the rapid mix. It is unclear if this final connection is needed, though, and it may be removed so that the larger tubing connects the T to the rapid mix directly.

For laboratory testing, water flows from the bottom of the chemical dosing tube to a plastic column with a pressure sensor at the bottom.  This pressure sensor gives readings of water height in the column, which can be converted into flow rates from the FC.