Scott,

I just received the following information from Enviropax concerning the tube settlers for your project.  You will see from the message, there appears to be two different quantities requested.  

I hope this information helps you in deciding what you will need to do.  When you finalize the design and requirements, we can get you a formal quote and include shipping information as well. 

So, look this over and let me know if you have any questions.  Have a good weekend.

Regards,

Jim Devery
SF International Associates, Inc.
799 Bustleton Pike
Richboro, PA  18954-1353
Tel.:      215-357-3730
Fax:      215-357-5160
Cell:      215-630-8527
Email:   j.devery.sfia@gmail.com
Begin forwarded message:

From: "Brett Lees" <blees@enviropax.com>
Date: April 24, 2009 2:11:15 PM EDT
To: "'Devery, Jim'" <j.devery.sfia@gmail.com>
Subject: Four Communities Sed Tank / Tube Settlers
Jim -
 

The first set of e-mails talks about three (3) basins areas 2.159 m x 14.026 m (7'-1" wide x 46'-0" long), which is 326 ft2 x 3 = 978 ft2.  For our 3FT tube settlers in PVC construction this area would be about $31,500 FOB Salt Lake City, Utah.  It also talk about an upflow velocity of 100 m/day, which is about 1.8 gpm/ft2.  Typically we use about 2.0 gpm/ft2 for our 2FT tube settlers so this is a conservative application rate for our 3FT tube settlers.
 

The second set of e-mails talks about one (1) basin with the attached drawing showing the  area as 2.3090 m x 3.4899 m (7'-7" wide x 11' 5.5" long), which is about 87 ft2.  This much of our 3FT tube settlers in PVC would be about $3,100 FOB Salt Lake City, Utah.
 

I have attached a drawing of our 3FT tube settler.  We could make a custom height, if the quantities are enough.
 

Let me know what else you need.
Brett Lees
Enviropax, Inc.
Phone 801-263-8880
Fax 801-263-8898
blees@enviropax.com 
