## Slide 1: Non-Linear Chemical Dose Controller
Akta Patel Dale Johnson
Harrison Ko Karen Swetland
Kayti Curtis Monica Hill
Yoon Choi
Notes: Karen

## Slide 2: Watch our video!
Notes: Karen

## Slide 3: Clogging Experiment
Problems with dosing in current plants
  Constant head tank orifice is clogging
  Is it precipitate, foreign material, or influent water chemistry?
New orifices
  New design utilizes multiple orifices
  Small orifice size
Notes: Akta

## Slide 4: Clogging Experiment
-0.1 cm diameter orifice
-Alum at 125 g/L
-38.6 mL/s or 7 cm head difference
Notes: Akta

## Slide 5: Control Experiment - Water
Notes: Akta

## Slide 6: 24-Hour Alum Experiment
Spike indicates the possible presence of a clog
Notes: Dale

## Slide 7: Alum Experiment #2
-Some inconclusive evidence for clogging, which makes it difficult to estimate the frequency of clogging.
Notes: Dale

## Slide 8: Clogging Experiment
Next Step
  Inconclusive evidence of a clog
  Change orifice size: 1.01, 2.28 mm diameter to 1.587, 3.175 mm
  Recommend lower dose of alum: 125 g/L to 51 g/L
  Stock tank will have to be refilled more often
Notes: Dale

## Slide 9
Chart: Stock tank changing frequency
| 6.3 | 6 | 5.7 | 5.4 | 5.1000000000000005 | 4.8000000000000007 | 4.5000000000000009 | 4.2000000000000011 | 3.9000000000000008 | 3.6000000000000014 | 3.3000000000000007 | 3.0000000000000018
12.5 Kg. bag | 5.5115 | 5.787 | 6.0916 | 6.43 | 6.8083 | 7.2338 | 7.716 | 8.2672 | 8.9031 | 9.6451 | 10.5219 | 11.5741
25 Kg. bag | 11.0229 | 11.5741 | 12.1832 | 12.8601 | 13.6166 | 14.4676 | 15.4321 | 16.5344 | 17.8063 | 19.2901 | 21.0438 | 23.1481
50 Kg. bag | 22.0459 | 23.1481 | 24.3665 | 25.7202 | 27.2331 | 28.9352 | 30.8642 | 33.0688 | 35.6125 | 38.5802 | 42.0875 | 46.2963
Recommend using the 25 Kg bag
Notes: Dale

## Slide 10: Orifice and Dual Scale Design
5 to 25, 2.5 mg/L
20 to 100, 10 mg/L
Target Dosage
2.471 … 12.353mL/s
.618 to 3.088mL/s
Alum Flow Needed
Q=6.3L/s
Top View
30 100
5 20
7.5 30
10 40
12.5 50
15 60
20 80
17.5 70
22.5 90
PIVOT
Orifice1=3.175mm
Orifice2=1.5875mm
Orifice
Scale
What
We
Learned
Error from HL in Tube:
-Selected PVC as the tube material
-Make length as short as possible to 30-50cm
-Increased diameter to 9.525mm
Max error occurs at 10 mg/L – 5.5% w/ 50 cm, 1.3% w/30 cm
Orifice Diameter
Size
0.013 m … 0.313 m
PIVOT
Notes: Yoon

## Slide 11: Float Calculation
Alum Tube
FLOAT
CONSTANT
HEAD
TANK
Water Surface
L/2
X of Maximum Dosage
Slider
Assembly
Dosing Tube
We calibrate the lever arm at maximum dosage.
We find the weight of the Float that gives us the
correct alum at maximum dosage.
Notes: Yoon

## Slide 12: Float Calculation
Dosing Tube
FLOAT
CONSTANT
HEAD
TANK
Water Surface
L/2
X 8
Slider
Assembly
Slider
Assembly
Dosing Tube
Float Diameter=.102 to .152m
Float Height=.305m
CW
Notes: Yoon

## Slide 13: Rapid Mix Tube Construction
Previous rapid mix tube design was completed and designed for the Agalteca plant
  General MathCAD design was also completed for future plant implementation
A full-scale model of the rapid mix tube was constructed to test the ease and feasibility of the constructed system
Small scale mixing orifice presented a unique materials problem
  Solution: Bucket Lid material

## Slide 14: Rapid Mix Tube Future Experiments
Series of experiments proposed to test the necessity and effect of rapid mix on effluent water turbidity
  Alum Accumulation Tank
  Change current rapid mix system out for the new design
  Is inadequate rapid mix having an adverse effect on effluent turbidity?

## Slide 15: AutoCAD Drawing of Prototype
Notes: Harri

## Slide 16
Assembled Doser with Hydraulic Components Attached
Notes: Monica

## Slide 17
Close up of dosing orifice
Notes: Monica

## Slide 18: THE END
Notes: Karen