# pH Control with Lime

## Abstract

According to alkalinity tests conducted with the source water of the Ojojona water treatment plant, the pH of the water is likely to drop to undesirable levels after the addition of alum. To raise the pH to levels that are optimal for coagulation, a lime feeder system that is capable of releasing saturated limewater for a period of more than 24 hours must be designed.  In an attempt to do this, various reactor designs were tested in the lab, including a vertical column, a conical vessel, a funnel connected to a column, and an inverted cone.  The inverted cone was found to be the most suitable design for maintaining a fluidized bed of lime.  The percentage of hydrated lime that was available for dissolution in these experiments was only about 50-60%.  A scaled-up version of the cone reactors for use in Ojojona would have a total top surface area ranging from 0.8 m2 to 1.2 m2, depending on how many feeders are constructed.  The required height for each cone is 1.8 m.  The system could potentially work in Honduras because it requires little maintenance, except for the addition of lime.  However, suitable techniques for constructing the cones using inexpensive local materials must be developed.

## Background

The effectiveness of coagulation in water treatment is highly dependent on pH. When alum is added to water and hydrolyzed, many different species of aluminum hydroxide polymers are formed. Each polymer differs in size and charge concentration and has a different effect on coagulation. The relative amount of each polymer species depends on the pH of the water {{32 Faust, S.D. 1983; }}. An objective of the Ojojona plant is to ensure that the pH of the water remains in the range of 6-8 for optimal coagulation. This has the advantage of reducing the quantity of alum required and also improving the quality of the floc formed. Another concern with low pH is the increased corrosiveness of acidic water and the health risks associated with leaching metals in the distribution system.

To assess the buffering capacity of the source water, the acid neutralizing capacity (ANC) of the actual water samples from two collection points on the existing supply system in Ojojona were measured. The ANC of the samples from collector two and collector three were 0.0014 eq/L and 0.00056 eq/L, respectively. From the titration results, the effect of alum addition on the pH of the water can be predicted (Figure 1 and Figure 2). The results from collector 3 suggest that although the initial pH of the source water is 6.5, the addition of alum may reduce the pH to undesirable levels. This suggests that for effective coagulation of the source water at Ojojona, a sustainable and easily maintainable system needs to be designed to raise the pH of the water before the coagulation process.

To the best of our knowledge, the chemicals that are locally available and inexpensive for pH adjustment in Honduras include calcium oxide (known as live lime, or cal viva), calcium hydroxide (known as dead lime, or cal muerta) and calcium carbonate (limestone). Although both lime and limestone are insoluble, saturated limewater can reach a pH of approximately 12.5 while limestone can only raise the pH of water up to approximately 8. For this reason, the pH research team has been testing different lime feeder designs. The objective is to design a reactor that can constantly output saturated limewater for at least 24 hours so that fresh lime need only be added daily. The limewater can then be mixed with the water flowing into the plant to raise the pH to 6.5-8.5 as desired.  The 24 hour period is based on the assumption that the plant operator will check on the plant at least once per day.

20

mg/L

alum

40

mg/L

alum

60

mg/L

alum

80

mg/L

alum

Figure 1.  Change in pH with the addition of alum to source water from Collector 2.

20mg/L

alum

40mg/L

alum

60mg/L

alum

80mg/L

alum

Figure 2.  Change in pH with the addition of alum to source water from Collector 3.

## Chemistry

### Alum

Aluminum sulfate [Al2(SO4)3·18H2O, MW = 666 g/mol] dissolves in water to produce 6 moles of H+ ions per mole of alum (Eq. ).

Al2(SO4)3 + 6H2O  2Al(OH)3 + 6H+ + 3SO4-2

Every mole of alum releases 6 moles of protons and thus the equivalent weight of alum is 111g/eq. Given a maximum alum dose at the plant of 80 mg/L, the amount of equivalence that must be countered with lime is calculated to be 7.2 x 10-4 eq/L.

### Hydroxides

Two forms of lime, calcium oxide and calcium hydroxide, were used in our experiments. Since calcium oxide reacts with water to form calcium hydroxide (Eq. ), both limes should yield similar experimental results. Calcium oxide [CaO, MW= 56 g/mol] was used for our initial experiments with the first three reactor designs. However, since the hydrolysis of calcium oxide is highly exothermic, calcium hydroxide was chosen for use at the Ojojona plant for safety reasons.

CaO + H2O  Ca(OH)2

Calcium hydroxide [Ca(OH)2, MW = 74g/mol] dissolves in water to form two hydroxides (Eq. ).

Ca(OH)2  Ca2+ + 2(OH-)

With an equivalent weight of 37 g/eq, the mass of lime needed to counter the 7.2 x 10-4 eq/L of alum is calculated to be 0.027 g/L.

Calcium hydroxide has an extremely low solubility of about 1.65 g/L at 20 degrees Celsius.  Despite this fact, hydrated lime can provide significant neutralizing power because of its production of two OH- ions after dissociation.  It is interesting to note that the solubility of lime increases as temperature decreases, with the highest solubility being at 0 degrees Celsius.

### Raising pH to 8 or 8.5

The increase in ANC required to raise the pH from 5.5 to 8 can be calculated using Equations -.  If the sum of all the components of the carbonate system, CT, is assumed to be zero, the rise in ANC is 4.15 x 10-6 eq/L. Using the equivalent weight of calcium hydroxide, we can calculate that the amount of lime required for this reaction is 1.5 x 10-4 g/L. However, if the hardness of the water is considered (CT = 0.02 mol/L), the corresponding rise in ANC is 2.11 x 10-5 eq/L.  The change in ANC is greater in the latter case because the bicarbonates and carbonates act as buffers.

where 	Kw = 10-14 M

K1 = first dissociation constant for carbonic acid = 10-6.3

K2 = second dissociation constant for carbonic acid = 10-10.3

CT = sum of all the components of carbonate system – carbonates, bicarbonates, carbonic acid.

### Buffering System

Since pH is a logarithmic measure of the concentration of H+ protons, a small change in the ANC can lead to large changes in pH when the pH is close to neutral.  To avoid overshooting and undershooting of pH adjustment with lime, an additional chemical such as sodium bicarbonate should be added to provide buffering capacity to the water.  With an acid dissociation constant, pKa, of 6.33, bicarbonate is a suitable buffer for maintaining the pH at 6.5 (Eq. ).  As a result the bicarbonates will dampen the effect of errors in lime addition and help maintain the pH close to the target.

H2CO3  H+ + HCO3-

## Methods

### Materials

The calcium oxide used for our experiments was lab grade calcium oxide from Fisher Scientific.  The calcium hydroxide used was hydrated lime for horticultural purposes, purchased from Agway, Ithaca, NY.

### Apparatus

To achieve a functional lime feeder design that is capable of releasing saturated limewater for over 24 hours, a series of apparatuses with varying sizes and shapes was tested.  These included a 1” column, a conical vessel, a funnel connected to a column, and an inverted cone reactor.  Each reactor provided new insights into the characteristics of lime and hydraulic mixing, leading us closer to the final, potentially functional design of an inverted cone

The first design tested was a simple 1” column upflow reactor, where the influent entered through the bottom and the effluent flowed out through the top (Figure 3).  A pH probe was inserted into the effluent tubing for constant monitoring of the pH.

Figure 3.  Lime feeder design 1: Column upflow reactor.

Next, a vessel with a cylindrical section and a conical section at the bottom was used (Figure 4). Here, the influent entered the vessel through a vertical metal rod that was centered and placed approximately 2-3 inches from the bottom of the vessel. A pH probe was also suspended at the surface of the water to monitor the pH of the effluent.

28cm

15cm

3cm

D = 17cm

Inlet

Outlet

Figure 4.  Lime feeder design 2: Conical vessel. Influent enters through metal rod and effluent exits through outlet at the top of the vessel.

As a combination of the first two designs, the next apparatus that was tested was a funnel glued to a long column (Figure 5). The influent came through the bottom of the column and flowed out of the side of the funnel. A pH probe was clamped to the side of the funnel at the level of the effluent for pH monitoring.

Figure 5.  Lime feeder design 3: Funnel-column.

To allow for a more gradual change in the slope of the vessel walls, the last apparatus used was an inverted traffic cone. The influent was brought in through a vertical metal pole that was centered and placed about an inch from the bottom of the cone. Again, a pH probe was placed at the outlet to monitor the effluent pH.

84cm

83°

5cm

Influent

Effluent

D= 24cm

Figure 6.  Lime feeder design 4: Inverted Cone.

### Flow Control

The flow of Cornell tap water at a controlled temperature of 22 degrees Celsius was controlled by a pressure sensor, a head loss element, an accumulator, and a solenoid valve. The pressure sensor was connected to the data acquisition system and the solenoid valve was controlled with a closed loop PID (proportional, integral, derivative) controller. Water flows through the solenoid valve when it is in the “open” position. The valve is connected to the accumulator, which begins to pressurize as it is gradually filled. The flow rate increases as the pressure in the accumulator increases. The pressure sensor measures the pressure drop in a small tube as shown in Figure 7.  The computer converts this pressure drop into a flow rate. To make adjustments based on the desirable flow rate, the computer opens or closes the solenoid valve using a PID control algorithm.

Figure 7. Diagram of the flow measuring device used with all apparatuses.

### pH Measurements

Throughout all experiments, the pH of the effluent lime-water was constantly measured by a pH probe that transmitted data to a computer with data acquisition software. The probe was calibrated with pH 4, 7, and 10 buffer standards using the pH Meter software. The buffers were also replaced occasionally for more accurate calibration.

### Experimental Procedure

The steps followed for the experiments began with the preparation of a slurry of lime. The slurry removed any clumps of lime and allowed for a more homogenous mixture of lime throughout the apparatus. The flow rate was zeroed when there was no flow to obtain a more accurate flow rate reading. The pH sensor was placed at the level of the effluent for pH monitoring. As the slurry was poured into the top of the apparatus, a very low flow rate was run through the system to prevent initial settling of the lime. To prevent the lime from flushing out, it was left to settle for about 30 minutes before the flow rate was increased. Throughout the actual experiment, manual measurements of the flow rate were taken periodically and the pH of the effluent was monitored.  A pH exceeding 12 was a good indicator of saturated limewater in the effluent.  Thus, experiments were usually terminated upon observing a drop below 12 in the effluent pH.

### Theoretical duration of high-pH given an initial mass of lime

With the assumption that the effluent from a reactor consists only of saturated limewater and no lime particles, it is possible to perform a simple calculation to estimate how much lime has left the system after a certain period of time, or similarly, how long an experiment can last given an initial mass of lime.

First, the ANC of saturated limewater (pH ~ 12.5) can be calculated using Equation .  If Ct is assumed to be zero, the ANC of saturated limewater is calculated to be 0.0316 eq/L. However, if the alkalinity of Cornell’s tap water (~100 mg/L CaCO3) is accounted for, the ANC is found to be 0.034 eq/L {Bolton Point - Municipal Water System, 2005}.  As shown in Equation , the mass of lime that theoretically leaves the system in a given period of high-pH effluent can be calculated based on flow, duration, and the equivalent weight of lime. Similarly, given an initial mass of lime, we can calculate the theoretical period of time that the system can output saturated limewater (Eq. ).  Because we are considering the ANC of the water due to lime only, we used the assumption that Ct is zero in these theoretical calculations.

where: 	Mexit = theoretical mass of lime exiting system (g)

Q = flow rate through reactor (L/min)

Tobs = duration of high pH (min)

ANClime = ANC of saturated lime (eq/L)

EqWtlime = Equivalent weight of lime (g/eq)

T = theoretical period of time with high pH (min)

Minit = Initial mass of lime added to the reactor (g).

## Results

To determine the optimal system for feeding high pH limewater for a period of more than 24 hours, tests were carried out on a series of reactors with different shapes – a vertical column, a vessel with a conical bottom, a column leading into a funnel, and finally an inverted cone. The performance of each reactor was assessed in order to improve the design. New knowledge acquired from experimenting with one reactor often prompted the test of another reactor design with a different shape.

### Column

#### Hypothesis

The initial hypothesis was that a minimal upflow velocity of water through the reactor is required for the lime particles to stay in suspension and slowly dissolve to saturate the influent water. According to experiments conducted previously with the conical vessel, an upflow velocity of 1.7 cm/min is sufficient for carrying an initial mass of 170 g out of the system {Reiss, Taylor 2005}. It was expected that with a similar upflow velocity in a 1” column (approximately 10 ml/min flow), the lime would behave in the same way, guaranteeing a constant flow of saturated limewater out of the system.

#### Results

With an initial flow rate of 12 ml/min, the pH stayed at its maximum for approximately 3.5 hours before dropping. After increasing the flow to 25 ml/min, the pH rose back up to its maximum for approximately 1.5 hours before dropping again (Figure 8).

Figure 8.  Change in pH throughout an experiment with the 1” column design.  A flow rate of 12 ml/min was used for the first ~5 hours, and 25 ml/min was used for the remainder of the experiment.

#### Interpretation of Results

From experiments with the column, it was concluded that the theoretical upflow velocity seems to work in keeping only the finest lime particles suspended.  These are the particles that dissolve to provide saturated limewater in the initial period of the experiment. After a while, however, all the lime particles settle and the water flows in a preferential path through the bed of lime. This limits the amount of contact between the water and the lime particles.

To increase the dissolution rate and to maximize contact with lime particles, the lime should be in a fluidized bed. While this can be achieved by increasing the flow rate in the 1” column, the higher flow rate will also cause all the particles to flush out at the outlet. Thus, an ideal reactor would have a region at the bottom where most of the lime is stored and mixed, and a more quiescent region at the top with fewer lime particles. Since the amount of mixing is correlated with the velocity of the water and the velocity is inversely proportional to the cross-sectional area of the reactor, a vessel with increasing diameter from bottom to top seems to fulfill our objective.

### Conical Vessel

#### Hypothesis

The next reactor that was tested was a vessel with a conical bottom (Figure 4). In this case, the lime particles were expected to stay in suspension at the bottom, where the upflow velocity of the water is the highest, and to slow down as they reach the region with constant diameter.

If it is in constant suspension, all the lime was expected to dissolve slowly and leave the system after a period of time. The effluent pH should stay at 12.5 as long as there is suspended lime remaining in the reactor.

#### Results

A test run was conducted with 400 g of calcium oxide, which was expected to last for approximately 12.5 hours at a flow rate of 0.6 L/min. The upflow velocity was approximately 85 cm/min at the very bottom, and 2.6 cm/min at the region of constant diameter. The pH stayed constant initially for approximately 5 hours before dropping (Figure 9). Since there was no mixing observed at the lime-water interface, the influent rod was moved up closer to the surface to induce more mixing. This caused the pH to rise back to its maximum for about 3 hours before dropping again (Figure 9). At this point the lime had all settled, suggesting that the mixing in this system is inadequate for keeping the lime in suspension.

Figure 9. Change in pH throughout experiment with conical vessel.

#### Interpretation of Results

The estimated duration of high pH effluent for this experiment was estimated to be 12.5 hours. In actuality, the pH started dropping after only 68% of the lime left the system. We presumed that the reason for this was that the settling of the lime had prevented complete dissolution.

From our observations, the mixing at the bottom of the conical vessel was insufficient to keep all the lime suspended. Moving the influent rod up and down with the lime would ensure mixing at the interface, but it would add mechanical complexity to the system. In addition, although there is mixing at the interface, the geometry of the vessel prevents thorough mixture of all the lime in the system. While the maximum upflow velocity is calculated to be 85 cm/min, this velocity drops rapidly to 2.6 cm/min within a distance of 15 cm up the cone.

Thus, in order to generate more turbulence at the bottom of the reactor, a greater region with high upflow velocities and small cross-sectional areas towards the bottom of the reactor is needed. This would create a fluidized bed that maximizes the dissolution rate of the lime particles.

In addition, according to our observations with the conical vessel, lime particles can still be carried out of the effluent at an upflow velocity of 2.6 cm/min.  This suggests that in order to obtain saturated limewater that is completely devoid of lime particles, the upflow velocity at the top of the reactor should be decreased

### Funnel-Column

#### Hypothesis

To provide a greater region of mixing for the lime, the next reactor we tried was a 1 ¼” column connected to a 9” diameter funnel (Figure 5). The hypothesis was that the lime would be in constant suspension inside the column and slow down as it moved through the funnel. At a point where the lime’s sedimentation velocity exceeded the upflow velocity, the particles will stop moving upwards and a sludge blanket will form inside the funnel. The funnel thus provides a storage area for the lime. As the lime is constantly mixed with the water, it is expected to slowly dissolve with time. The water should remain saturated with lime until most of the particles have dissolved or exited the system.

#### Results

Two experiments were conducted using 200 g of CaO, which were expected to last for 37.7 hours at 100 ml/min. This flow rate corresponds to an upflow velocity in the column of 12.4 cm/min, and a velocity at the top of the funnel of 0.28 cm/min. The effluent remained saturated with lime for approximately 20 hours in the first run, and approximately 25 hours in the second run (Figure 10).

A third experiment was conducted to test whether adding half the amount of lime would provide saturated limewater for half the amount of time. With 100 g of lime, the pH started to drop after 7 hours into the run, which is significantly earlier than the 10 to 12 hours that was expected (Figure 10).

Throughout all experiments, the lime at the funnel spout had to be mixed periodically to prevent clogging of the system.  If this was not done, it was observed that the column would start clearing up as more and more lime accumulated in the funnel.

Figure 10.  Change in pH over time for three experiments with the funnel-column. For the 100g and 200g 2nd run experiments, the pH started dropping after approximately 7 and 20 hours, respectively. pH data was collected every minute.

For all three experiments, the pH started dropping even though the lime was still fluidized in the column. Though the particles had become noticeably bigger towards the end of the experiments, the total amount of white solids in the system had not decreased noticeably.

#### Interpretation of Results

According to our calculations, 200 g of calcium oxide (7.14 mol OH-) should have provided enough equivalents for the effluent pH to remain high for ~37.7 hours. In the period of 25 hours that was actually observed, we can estimate that 133 g of lime (4.74 moles OH-) should have left the system. This assumes that the effluent did not contain lime particles. Theoretically, then, only 67 g of lime should have remained in the system after 25 hours. From our observations however, there was no marked decrease in the amount of lime in the system after the run. This discrepancy suggests that the white solids remaining in the reactor may actually have been calcium carbonate, or lime particles coated with calcium carbonate. A calcium carbonate coating would drastically decrease the dissolution rate of the lime. This may explain why the pH begins to drop even before all the lime has left the system. It also suggests that the observed increase in particle size throughout the experiment may be due to the calcium carbonate coating.

Instead of lasting half the time of the 200 g experiments, the 100 g experiment outputted high-pH effluent for only 7 hours. This suggests that the duration of high pH depends not only on the flow rate and initial mass of lime, but also the concentration of lime in the reactor.  Further experiments should be conducted to test this idea.

While the funnel-column reactor was able to fluidize the lime and provide saturated limewater for over 24 hours, this was only possible because the spout was manually unclogged throughout the experiment. Since an ideal reactor would run without maintenance for at least 24 hours, the funnel-column is an inadequate design. Our hypothesis is that the clogging is due to the sudden change in cross sectional area at the entrance of the funnel. Because the upflow velocity through the column is much greater than that through the funnel, the lime particles that are carried into the funnel cannot fall back into the column. Eventually, in accordance with our observations, all the lime particles leave the column and accumulate in the funnel. Based on these results, we postulated that the sudden change in diameter of the reactor should be eliminated to prevent clogging.

### Inverted Traffic Cone

#### Hypothesis

Since a conical shape gives a gradual increase in cross-sectional area, the next reactor design we tried was an inverted traffic cone (Figure 6). Most of the mixing would occur at the bottom of the cone, where the cross sectional area was relatively small. We expected a sludge blanket to form where the upflow velocity of the water equaled the sedimentation velocity of the lime. The height of the sludge blanket was also thought to be a function of the initial mass of lime added.

#### Results

An initial experiment was conducted with 500 g of hydrated lime and a flow rate of 880 ml/min. This corresponds to an upflow velocity ranging from 43 cm/min to 1.9 cm/min. The pH remained at its maximum for approximately 5 hours, which is 3 hours less than what we would expect if all the lime was used up (Figure 11). The ratio of the actual amount to the theoretical amount of lime that exited the system in 5 hours was calculated to be 0.59.

Figure 11.  Change in pH with inverted cone design – flow rate = 880ml/min; initial lime mass = 500g.

In an attempt to prolong the period of high pH effluent, an experiment using 1800 g (48.7 mol OH-) of lime was conducted. This system provided saturated limewater for approximately 18 hours, during which an estimated 18.7 moles of OH- exited the system (Figure 12). The ratio between the actual and theoretical amounts of lime that exited is calculated to be 0.39 in this case. At the beginning of this experiment, excessive flow rates had flushed out unknown amounts of lime particles from the system. If this had not happened, we would have expected the period of high pH effluent to have lasted longer.

Figure 12.  Change in pH over time for experiment with inverted cone: flow rate = 550 ml/min; initial lime mass = 1850 g.

A final experiment was conducted with 1000 g of lime using a flow rate of approximately 670 ml/min, corresponding to an upflow velocity at the top and bottom of 1.5 cm/min and 34 cm/min, respectively.  The pH remained high for approximately 12 hours, corresponding to a departure of 15 moles of OH- (Figure 13). The ratio of the lime that exited to the lime that should have exited prior to a drop in pH is calculated to be 0.56.  ANC samples were also taken periodically throughout the experiment.  As seen in Figure 13, it took more than an hour for the ANC to stabilize, indicating that lime particles were being carried out in the effluent at the initial stages of the run.

Figure 13.  Change in pH and ANC with an inverted cone experiment: flow rate = 670 ml/min; initial lime mass = 1000 g.

The upflow velocity at the sludge blanket was estimated to be 1.65 cm/min.  Although it was impossible to observe the mixing of the lime through the opaque traffic cone, the obvious movement of the lime at the lime-water interface was a good indication that the particles were being well-mixed throughout the entire height of the cone. The level of the sludge blanket remained relatively constant for the first 10 hours of the experiment, staying approximately 1” below the outlet.  After 10 hours, however, the sludge blanket started rising, reaching closer to the outlet.  To prevent lime particles from flowing out, the flow rate had to be decreased to approximately 600 ml/min at this point.

#### Interpretation of Results

As hypothesized, the inverted cone did not clog like the funnel-cone design. The lime remained fluidized throughout the experiments, even after the drop in pH.  This suggests that a cone-shape is ideal for providing a sustainable, low-maintenance system of turbulent mixing at the bottom and quiescent flow at the top.

In the last experiment described, lime particles were initially carried out in the effluent.  This was probably because the sludge blanket was very close (1.5” to 2.5”) to the surface of the water throughout the entire experiment.  This means that it was easy for the particles to be sent out with the effluent, especially with the sudden changes in flow rate during flow adjustment in the beginning of the experiment.  To avoid this, the lime should be allowed to settle for more than an hour before the flow is started.  This requirement is onerous since it would increase the time that the plant operator would have to spend at the plant.

Flows ranging from 600 ml/min to 740 ml/min were observed throughout the experiment, indicating that there were large fluctuations in flow.  This explains the vertical movement of the sludge blanket and suggests that a certain zone at the top of the cone should also be allocated as freeboard to minimize the risk of overflowing lime.

According to our results, approximately 50% to 60% of the initial lime added to the system can dissolve and saturate the influent water. Since one has to add almost twice the amount of lime to compensate for this inefficiency, the current inverted traffic cone reactor does not have the capacity to hold enough lime to sustain a run of more than 24 hours.

### Summary of Results

A summary of the experimental results for the lime feeder designs are presented in Table 1.

| Table 1. Summary of results from selected lime feeder experiments. Minit is the initial mass of lime added to the system; Q in black represents measured flow; Res. Time is the residence time of the water; Tobs is the observed duration of high-pH while T is the theoretical duration; Mexit/Minit is the ratio of the mass of lime that exits the system to the initial mass; Vsb is the upflow velocity at the sludge blanket; Vbottom is the velocity of the water at the very bottom of the vessel. |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Reactor | Lime Type | Minit (g) | Q (L/min) | Res. Time (min) | Tobs (hr) | T (hr) | Mexit/ Minit Ratio | Vsb (cm/min) | Vbottom (cm/min) |
| HalfCone | CaO | 400 | 0.6 | 12.48 | 9 | 12.56 | 0.72 |  | 84.9 |
| Funnel | CaO | 200 | 0.1 | 46.10 | 20 | 37.67 | 0.53 | 0.71 | 12.4 |
| Funnel | CaO | 200 | 0.1 | 46.10 | 25 | 37.67 | 0.66 | 0.71 | 12.4 |
| Funnel | CaO | 100 | 0.1 | 46.10 | 7.75 | 18.84 | 0.41 |  | 12.4 |
| Cone | Ca(OH)2 | 300 | 0.4 | 31.95 | 6 | 10.69 | 0.56 | 1.5 | 19.6 |
| Cone | Ca(OH)2 | 300 | 1 | 12.78 | 1.25 | 4.28 | 0.29 |  | 49.0 |
| Cone | Ca(OH)2 | 500 | 0.88 | 14.52 | 4.75 | 8.10 | 0.59 | 2.35 | 43.1 |
| Cone | Ca(OH)2 | 1800 | 0.55 | 23.24 | 18 | 46.65 | 0.39 |  | 26.9 |
| Cone | Ca(OH)2 | 1000 | 0.52/0.84 | 22.02 | 11 |  | 0.47 |  |  |
| Cone | Ca(OH)2 | 1000 | 0.67 | 20.00 | 12 |  | 0.56 | 1.65 | 32.8 |

## Scaling up – Ojojona Plant

Based on our experimental results with the four different reactor shapes, the inverted cone shows the most potential in steadily providing saturated limewater for over 24 hours. Hydraulic mixing in this reactor is sufficient to fluidize the lime and the system would require little maintenance except for the daily addition of lime. Thus, a scaled up reactor for the Ojojona plant can be designed based on the results from the inverted cone.  To reduce the size of the individual cones and to facilitate maintenance, a minimum of two lime feeders should be constructed.

### Assumptions

- The plant flow Q = 100 gpm ~ 378 L/min and the alum dose is 80 mg/L. The total required flow into the lime feeders is calculated as 8.6 L/min.

- The maximum upflow velocities in the cones will remain the same (33 cm/min).

- To calculate the minimum diameter at the top, we can use the velocity at the sludge blanket, which varies depending on the concentration of lime in the reactor.  Since we are keeping concentration of lime particles constant (Assumption 5) we should be able to use the same sludge blanket velocity.  In our cone experiments, the sludge blanket was very close to the surface of the water.  Thus, for ease of calculation and as a conservative estimate, we can use the minimum velocity (velocity at top diameter) as the sludge blanket velocity (1.33 cm/min).

- The amount of lime needed to counter the 393 equivalents of [H+] per day is 14.5 kg. Since only 50% of the initial lime added to the system will dissolve and exit the system, the reactors should be able to collectively store at least

- The concentration of lime particles in the systems should stay the same (78 g/L, as calculated by the volume of the traffic cone divided by the amount of lime added in the last experiment). A minimum height and volume of each reactor can be calculated based on this assumption. The angle of the cone is automatically determined by the height and the top diameter of the cone.

Using the assumptions above, we can calculate the required size of the reactors based on the number of reactors (Figure 14). The number of reactors built will depend on the cost and constructability. Based on the desired concentration of lime particles, the height of the cones would need to be at least 1.8 m.  An example reactor that could be built if 4 lime feeders are constructed is shown in Figure 15.  For detailed calculations, please refer to the MathCad calculation file (reference).

The challenge in the design is now in developing a construction technique for these cones using local materials.  Our findings suggest that a true conical shape should be used to guarantee constant suspension of the lime particles.

Figure 14.  The tradeoff between cone diameter and number of cones.  The top diameter is shown in blue dots and the bottom diameter is shown in red.

1.8m

83°

D= 0.11m

Effluent

D = 0.51m

Figure 15. Possible cone reactor for the Ojojona water treatment plant.  These dimensions would be suitable if four lime feeders (three in-line) were constructed for the plant.

## Discussion

### Reactor design

Since lime has a very low solubility, the success of a lime feeder design is highly dependent on its ability to achieve maximum lime dissolution rates.  This can be done if the lime is well-mixed with the influent and in constant suspension.

An inverted cone-shaped reactor seems to be the best design for a lime feeder. It creates mixing at the bottom to keep the lime fluidized while slowing down lime particles at the top to provide an effluent containing saturated limewater without lime particles. The gradual increase in diameter is a crucial factor in keeping the lime in suspension.  Since all the mixing is done hydraulically, the reactor requires little maintenance, except for the daily addition of lime.

A similar cone-shaped lime feeder was built for a water treatment plant in Brazil {{20 Schulz, C.R. 1984; }}.  The system uses cold water as the influent to generate saturated limewater.  This optimizes the process since the dissolution rate of lime increases as temperature decreases.

### Available Lime

According to our experimental results, only 50-60% of the initial lime added to the system will dissolve to make saturated limewater. One theory is that after a period of time, the calcium ions combine with carbonates in the water and form calcium carbonate coatings around the lime particles. This prevents further dissolution of the lime particles and decreases the duration in which high-pH effluent can be provided.  The discrepancy between the total and available amounts of calcium hydroxide has been seen in other processes using lime, such as water softening.  Some of the possible causes identified in the literature include the limited period of enforced intimate contact between the lime and the water; the coating of the lime particles, either with a shell of carbonate resulting from air slaking or the carbonates found naturally in the water; and the physical nature of the lime particles themselves {{37 Behrman, A. S. 1923; }}.

Another factor contributing to the difference between total and available lime is the presence of impurities found in quarried limestone, the raw material for making hydrated lime.  These non-lime components are commonly referred to as “grit” and do not contribute much to the ANC {{38 Ruskulis, Otto 1997; }}.  An acknowledged standard test for determining the percent of available lime is the ASTM Rapid Sugar Test, which is basically a titration using hydrochloric acid.  The addition of sugar increases the solubility of the lime through the formation of an intermediate product, calcium succrate.  This increases the accuracy and speed of the titration {{39 Cheney Lime & Cement Company; }}.  It would be interesting to use this standard to determine the availability of the hydrated lime we were using in the lab.

Although the presence of impurities in hydrated lime is inevitable, the calcium carbonate coatings are presumed to be the major contributing factor to the inefficiency of the lime particles in our lime feeder systems.  If the naturally-occurring carbonates in the water are the main contributors to the carbonate coatings, this phenomenon is expected to be less of a problem in Ojojona.  This is because the alkalinity of Cornell tap water, approximately 100 mg/L CaCO3, is much higher than the alkalinity of the source water in Ojojona, which was measured to be 1.14 mg/L ({{40 Arita, Sergio 2006; }}.

### Use in Ojojona

As described above, this lime feeder technology has showed promise in the laboratory and should be tested in the field.  However, some potential problems of the implementation and maintenance of the system in Honduras should be considered.  Firstly, pilot studies must be conducted to determine the characteristics of the lime in Honduras.  Different properties of the lime such as mesh size, availability, dissolution rate, and settling velocity will affect the performance of the system.  The source water in Ojojona will also have a different effect on the system compared to Cornell tap water.  These factors should be tested before designing the reactors for the plant.

In terms of maintenance, the reactor should be flushed out to remove the grit and calcium carbonate precipitate from the bottom of the cone.  The accumulation of these compounds over time may clog the system and make it harder to clean out.  In addition, scaling of lime in tubing or piping will occur and may need to be removed using mild acid.

Besides occasional maintenance of the reactors, the conical lime feeder system should be sustainable for use in gravity-fed plants such as the one in Ojojona.  Lime is a relatively inexpensive chemical, compensating for its inefficiency in dissolution.  Furthermore, a fluidized bed of lime can be constantly maintained in the reactor through hydraulic mixing alone.  Thus, potential problems associated with mechanical parts are avoided.

One drawback of the system, however, is that it may require daily maintenance. Since it is impractical to design a cone that is excessively tall, the maximum amount of lime in a cone would only be sufficient for use over 24 hours. With our current lime feed system, where the lime slurry is fed from the top of the cone, the operator would have to wait for the lime to settle before starting the flow. This increases maintenance time for the plant and may be an impractical requirement for the operator in Ojojona. To improve this system, a mechanism can be devised to feed the lime slurry at the bottom of the cone instead.  One possibility is feeding the slurry through a tube or a pipe that extends down into the bottom of the cone.

The greatest challenge this system presents is the development of an economical technique for constructing cone-shaped reactors using local materials. If possible, potential ideas should be explored in Honduras with the input of local engineers and builders.

If the lime feeder proves infeasible as an option in Ojojona, pH can also be adjusted using more expensive, but soluble, bases that are easy to meter into the plant. One alternative that is available in Honduras is soda ash, or sodium carbonate (Na2CO3), which has a pH of approximately 11.6 in solution. The use of soda ash (9 Lempiras / kg) instead of lime will increase costs for the plant, but it will decrease complications since a solution form can easily be fed through a system identical to the alum feeder.