## Slide 1: Sedimentation Tank Hydraulics
Mahina Wang
Jill Freeman
Saied Khan
Matthew Hurst

## Slide 2: Introduction: What is floc blanket?
  A fluidized, highly concentrated bed of particles.
  Occurs when flocs switch from a state of differential settling to hindered settling.
Benefits of a floc blanket:
  Greatly improves the effluent turbidity by trapping small flocs.
  Reduces clean water waste from frequent draining of the sedimentation tank.
Notes: How does it form?
Flocs switch from a state of differential to hindered settling.
differential:
-Large flocs settle faster than small flocs.
-No interactions between flocs
-This means that very small flocs can escape through the plate settlers.
hindered settling:
-the flocs interact with each other
-settle at the same rate.
The floc blanket grows in size and density as it traps more and more particles.
A floc blanket greatly improves effluent turbidity.
Previous teams have determined that a minimum angle of repose of 23 degrees is needed on sedimentation tank sides for floc blanket formation.

## Slide 3: Floc Blanket Formation
  Adequate floc re-suspension by inlet jet
  Inclines to direct settling flocs towards inlet jet
Notes: -Previously, the minimum angle required to form a blanket was determined to be 23 degrees. Otherwise, sludge will build up on the slope until this angle is formed. This can be see in later experiments.
Explain how floc blanket forms. Jet resuspends flocs, and the flocs settle down to again be resuspended by jet.
First picture is differential settling. Jet resuspends flocs to full tank height.
Second picture: jet starts to resuspend flocs to a fraction of the tanks height.
3rd picture: floc blanket fully formed after about an hour. Note floc/water interface. Water above is significantly less turbid.

## Slide 4: Hypothesized Mechanism of Resuspension
Hypothesis: By counteracting the hydrostatic pressure of the solids with the hydrodynamic pressure of the jet we can effectively resuspend flocs

## Slide 5: Hydrostatic vs. Hydrodynamic Pressure
Hydrostatic
Pressure
Hydrodynamic
Pressure
Notes: Visual for hydrostatic vs. dynamic pressure.

## Slide 6: Challenge
Minimize the energy lost between when the jet exits the inlet and the point at which it contacts the returning solids.
Notes: This is because we suspect that the mechanism for floc resuspension is based on primarily 2 variables: the hydrostatic pressure of the solids on the incline, and the hydrodynamic pressure of the jet. The hydrodynamic pressure of the jet decreases as energy is lost, so this leads to less adequate floc resuspension.

## Slide 7: Current Sedimentation Tank
60 degree angle, flat bottom
geometry
Notes: UPDATE WITH NEW DESIGN TEAM DRAWINGS
Sed tank from side and front view. Explain how we model the tank.
-show where floc blanket forms

## Slide 8: Methods: Our Experimental Setup
Experimental Setup
Notes: -aerated water (distilled water to which purified water is added--as opposed to carbonated water) not in photo
-raw water: average influent turbidity at 100 NTU
-Turbidimeter measures turbidity and is connected to Process Controller, which can add either raw water or clay 30g/L depending on the turbidity
-concentrated kaolinite (low shrink-swell capacity)
-Run through a tube flocculator before being expelled through a downward-pointing jet suspended 10 cm from the bottom of the sedimentation tank (half inch crosssection)
-lit LCD screen behind tank
-Images of the tank acquired with camera at fixed time intervals and recorded using the LabVIEW data acquisition software
-1s/shot for background shots (adjustments)
-0.03s/shot for dye injection shots
-5s/shot when run flocs
-Used MasterProgram (image analysis software) to make a video (30 or 10 images/frame). Hope to at some point take measurable data about floc concentration (currently outside scope of what are doing now)
-Simulate a cross-section of the sedimentation tank in such a way so that we can image solids concentration (this is how spacing was chosen)
-Mention data and how it is analyzed
-we are not quantifying anything yet
-making observation based on images and video, generating hypotheses and durther developing bottom geometries based on these

## Slide 9: Our Model

## Slide 12
Dye Injecting Testing

## Slide 13: Experiments: Experiment 1: 60° Inserts, 10 cm Rounded Trench
Notes: Best geometry from summer experiments
-best floc blanket and little sludge buildup
-ran dye injection test from this-FAILURE (why? )
-observed turbulence at jet impact, which could lead to large energy loss/dissipation, entraining a lot of fluid, which also decreases jet velocity
-although upward velocity was achieved, the jet’s momentum decreased due to its impact with the bottom of the semi-circle
-energy dissipation decreases dynamic pressure (energy could otherwise contribute to the upward velocity of the jet stream)
-failure of this geometry shows that we can do better
-led to designs for new geometries
-OUR bottom geometry should:
-work for half plant flow rate and potentially work to re-suspend solids when plant flow has been turned off for an extended period of time
-minimize energy dissipation rate to minimize floc break-up (less turbulence)
-minimize fluid entrainment before contact with solids

## Slide 14: Experiment 1: 60° Inserts, 10 cm Rounded Trench
Dye Injection at 14 cm
Movie: 30 shots/s
Dye Injection at 50 cm
Movie: 10 shots/s
Notes: Movie 1: 0.03s/shot*30shots/s=0.9 (about real time)
Movie 2: 3x slower

## Slide 15: Experiment 2: Jet Reverser Without Lip
Pros
Reduced energy loss with “smoother” flow
Cons
Jet path deflection (instablity)
Potentially not utilizing all flocs

## Slide 16: Experiment 3: Jet Reverser With Lip
Pros
Difficult for solids to deflect jet path
2 Possible jet interaction points
Cons
Uneven flow around each side of the geometry
Inconsistent floc blanket

## Slide 17: Experiment 4: Splitting the Jet
Trouble in previous experiments:
Notes: -problems we encountered with previous experiments: with the double semi-circle geometry, jet was often unevenly split between the two sides. This led to unevenness in floc blanket on each side. How to make jet more precise?
-Also, flocs were unable to pass between sides due to the ½ inch width of the jet, so we were thinking that making the jet diameter smaller would help more accurately model the actual sedimentation tank.

## Slide 19: Experiment 4: Splitting the Jet
Notes: Used 2 3/8 outer diameter diameter acrylic? Pipes instead of a single ½ inch outerdiameter tube. The total cross-sectional areas turned out to be similar, so we adjusted the flow rates accordingly. (?)
Needed to add an extra flocculator and pump to assure that the flow rates were equal (simply splitting the stream could cause one side to flow faster, if there was a variation in head loss (?) on each side)
Positioned jet so that there was one tube exit on each side of the jet reverser.
Video illustrates that flow is distributed evenly on each side of the jet reverser.
---We also tested this with a floc blanket. **** RESULTS?
The narrower diameter tube was not sufficent enough to allow flocs to freely pass between each side of the tank. This is a limitation to our design.

## Slide 20: Experiment 5: Asymmetrical Geometry
Notes: Wanted to observe an experiment where the jet does not split: this might help floc resuspension since we do not lose energy where the jet splits. Since we are not splitting the jet, there will be twice the flow rate that can potentially be used for resuspension.
We have the jet entering the reactor at an angle, and a single semi-circle that will deflect the jet upwards. Flocs will be falling in the direction of the jet (these should enter the jet stream and be pushed upwards) and normal to the jet.
Also find a video with flocs, so we can illustrate the differences in floc resuspension?

## Slide 21: Experiment 5: Asymmetrical Geometry
Notes: We also ran this experiment to observe failure: Slowly decreased the flow rate in 60 mL/min intervals to see the flow rate at which failure occurs. The lower this flow rate, the better the geometry.
Failure is defined as: Flocs passing the jet stream and the reactor. Flocs building up on the incline.
We able to take the flow rate much lower than we thought: 60 mL/min (?)
We plan to run this test on previous geometries as well to determine which one is the least likely to fail.
**This video validates the hypothesis that the jet does deflect if the dynamic pressure is too low and solids can enter the path. Jet deflection is a sign of scouring and entrainment of solids.

## Slide 22: Future Work
Ideas for Future Experiments:
Quantifying Hydrostatic and Hydrodynamic Pressure
Designing a Floc Weir
Atima final designs in one month
Notes: 1. Quantifying Analysis: ?
2. Measuring hydrostatic pressure: we want to measure the effects of hydrostatic pressure due to solids built up on the incline, find a relationship between hydrostatic pressure and dynamic pressure, and connect this to bottom geometry failure
-hydrostatic pressure: pressure exerted by a fluid at equilibrium due to the force of gravity (rho*g*h)
-related to the height and density of the solids built up on the incline
-be specific on what you are measuring and how you will use this data to quantify your observation
-dynamic pressure: q=1/2*rho*v^2; closely related to the kinetic energy of a fluid particle, one of the terms of Bernoulli’s equations, essentially an equation of energy conservation for a fluid in motion
3. Designing a floc weir: we need to determine the appropriate height of the floc weir and the necessary rate of sludge removal from the hopper to keep the tank at equilibrium. Previous research done by Matthew Hurst (masters thesis) argues that the overall particle removal efficiency improves with increasing floc blanket depth up to 45 cm.
-45 cm=initial height of our floc weir, which will ensure the highest possible removal efficiency for the smallest floc blanket, thereby saving space in the sed tank
-floc weir should be higher than flock blanket when first forms so it does not disrupt formation
-draw water at a constant rate from another pipe
4. Atima final designs in one month: will be sending most adequate bottom geometry by then

## Slide 23: Q & A
Notes: 1. Quantifying Analysis: ?
2. Measuring hydrostatic pressure: we want to measure the effects of hydrostatic pressure due to solids built up on the incline, find a relationship between hydrostatic pressure and dynamic pressure, and connect this to bottom geometry failure
-hydrostatic pressure: pressure exerted by a fluid at equilibrium due to the force of gravity (rho*g*h)
-related to the height and density of the solids built up on the incline
-be specific on what you are measuring and how you will use this data to quantify your observation
-dynamic pressure: q=1/2*rho*v^2; closely related to the kinetic energy of a fluid particle, one of the terms of Bernoulli’s equations, essentially an equation of energy conservation for a fluid in motion
3. Designing a floc weir: we need to determine the appropriate height of the floc weir and the necessary rate of sludge removal from the hopper to keep the tank at equilibrium. Previous research done by Matthew Hurst (masters thesis) argues that the overall particle removal efficiency improves with increasing floc blanket depth up to 45 cm.
-45 cm=initial height of our floc weir, which will ensure the highest possible removal efficiency for the smallest floc blanket, thereby saving space in the sed tank
-floc weir should be higher than flock blanket when first forms so it does not disrupt formation
-draw water at a constant rate from another pipe
4. Atima final designs in one month: will be sending most adequate bottom geometry by then