## Slide 1
Step-Tapered Inlet Manifolds
Team CAP’D
Chris DeFeo
Akta Patel
Patrick Farnham
David Chang

## Slide 2: Importance of Properly Designed Manifold
Flocs settle out if scour velocity is not maintained
  Especially important if using pipe manifold
Need equal flow distribution
  Floc blanket
  Equal loading on plate settlers
Notes: akta

## Slide 3: Simple Manifold Design
Untapered inlet pipe
15.24 cm (6 in) diameter
Uniform port size

## Slide 4: Problems with Untapered Manifold
VManifold < Vscour
 Floc breakup, settling within manifold
Notes: akta

## Slide 5: Step-Tapered Manifold Design Goals
Attempt to achieve uniform port flow while also minimizing energy dissipation rate
Keep manifold velocity greater than scour velocity
Notes: akta

## Slide 6: Step-Tapered Manifold Design
Agalteca design constants
  Plant flow rate, sedimentation tank length
Use eccentric reducers
  Keep ports eqidistant from sed tank bottom
  Maintain sludge scouring on sed tank bottom
Added pressure recovery
to piezometric head
Entrance region losses?
Notes: dave

## Slide 7: Force Balance
For a fully-developed flow condition
Notes: dave

## Slide 8: Laminar and Turbulent Conditions
Laminar Equation:
Turbulent Equation:
Notes: Looked up for flat plate
Patrick

## Slide 9: Shear vs. distance
Notes: Shear always less than predicted by fully dev. – we used DW equation- conservation energy dissipation…less than prediction.
patrick

## Slide 10: Manifold Velocity
Notes: Added major loss and pressure recovery term.
Designed manifold so that manifold velocity is above scour velocity.
Patrick?

## Slide 11: Varying port spacing
Notes: Length of manifold given by dimension of sed tank. Ports constant diameter. Pipe diameter determined by given sizes.
How energy dissipation varied with different spacing and total port area.
Bigger port spacing….lower energy dis. But worse flow distribution…but sucks anyway
akta

## Slide 12: Varying total port area
Notes: Bigger ports- worse flow, lower energy dissipation
akta

## Slide 13: Final Design
14 ports with 15 cm spacing
Total port area of 320 cm2 (0.202 m diameter ports)
Pipe Diameter |  | Pipe Length
(cm) | (in) | (m)
15.25 | 6 | 0.30
10.16 | 4 | 1
7.62 | 3 | 0.30
5.08 | 2 | 0.30
Notes: Chris

## Slide 14: Energy Dissipation Rate
Notes: With b= 15cm and port area of 3202
chris

## Slide 15: Port Flow Rate
Notes: chris

## Slide 16: Problems
Port flow not uniform
Energy dissipation higher than AguaClara recommended maximum energy dissipation rate of 6 mW/kg
Ports large compared to smallest pipe size (1.8 in. diameter port compared 2 in. pipe diameter)
Notes: patrick

## Slide 17: Tapered Manifold Cost Analysis
Pipe Diameter` |  | Price (USD/m) | Pipe Length (m) | Cost (USD)
(cm) | (in) |  |  | 
15.25 | 6 | 22.61 | 0.30 | 6.8
10.16 | 4 | 12.86 | 1 | 12.9
7.62 | 3 | 8.99 | 0.30 | 2.7
5.08 | 2 | 4.43 | 0.30 | 1.3
 |  |  | TOTAL | 23.7
Eccentric Reducer Size |  | Price (USD) |  | 
cm x cm | in x in |  |  | 
15.25 x 10.16 | 6 x 4 | 35.5 |  | 35.49
10.16 x 7.62 | 4 x 3 | 30.5 |  | 30.49
7.62 x 5.08 | 3 x 2 | 25.5 |  | 25.49
 |  |  | TOTAL | 91.47
 |  | PIPE + REDUCER | TOTAL | 115
2 Sedimentation Tanks |  |  |  | x 2
 |  |  | TOTAL COST | $230
Notes: chris

## Slide 18: What we learned and future explorations
Manifolds are tricky!
Continuously taper
Changing design constraints
  Maintaining scour velocity
More thorough analysis of losses within manifold
Notes: Dave

## Slide 19: Questions?
“Tapir”ed
Step
Inlet
Manifold

## Slide 20: References