## Slide 1: Design Team
Annie Ding, Anthony Andrews, Bonnie Schiffman, Brooke Pian, Julia Morris, and Kelly Huang

## Slide 2: Automated Design Tool (ADT)
Access to customized plant designs
  User inputs
Key to continuing scalability
Open Source Engineering
AguaClara Design Philosophy
Notes: Online interface that provides access to customized plant designs, invent scalable, reproducible tools that can be combined to form a complete water treatment plant.

## Slide 3: Automated Design Tool
Mathcad
Calculations
Mathcad
Drawing Files
User Inputs
LabVIEW
Plant
Design
AutoCAD
MS Word
Notes: User places inputs, design tool sends a request to the AguaClara server to produce a spreadsheet of all variables relevant to the plant design, and the values assigned to each of them. These include pipe diameters, wall dimensions, and baffle dimensions and placement. The ADT uses these variables to scale plant components in AutoCAD to create a complete, three dimensional design of the entire plant and its components.

## Slide 4: The Drawing

## Slide 5: Overall Design Tasks
  Incorporating new research progress into the design
  Designing plants for a greater range of flow rates
  Making our designs more easily understood
  Communicating with the team in Honduras and with new implementation partners to address concerns
Notes: Design or constructability concerns

## Slide 6: Automated Section Cuts
  Contact with AutoDesk Engineer
  Customized AutoCAD module
    Loadable (ex: Add-on), no use of dialog box
    Consistent layer colors from source
Section plane shown in 3D view
Finished section cut

## Slide 7: High Flow Modifications: Rapid Mix
Bonnie Schiffman and Brooke Pian
Spring 2013

## Slide 8: Introduction
A new flow metering system and coagulant rapid mix design is necessary for AguaClara to be able to serve larger communities.
For high flow plants, the current LFOM design is not ideal.

## Slide 9: Previous Design
Tori Klug, 2012
Notes: Previous work on high flow plant designs resulted in the design of an LFOM mica sheet, which would have water flow from the entrance tank into a rapid mix channel rather than a PVC pipe.

## Slide 10: Initial Schematic
Macro-mixing and Coagulant Dosing
Micro-mixing
LFOM sheet
Notes: Our task is to continue with the rapid mix channel design to provide rapid mixing of coagulant for high flow plant designs. We need to determine the geometry of the channel that will flow from the entrance tank to the bottom of the flocculator and design for macro- and micro-mixing; thus, we need to understand which constraints are most important. We need to consider where coagulant dosing will occur and include dosing into the design. We need to determine at which point the transition from LFOM pipe to LFOM channel will occur by evaluating hydraulics, construction and cost of materials needed, and include this switch into the design.

## Slide 11: Channel Size and Macro-Mix Orifice
To find channel size we assume total head loss is 5cm and minor losses rein: inflow, around a bend, through an orifice sheet (2), and outflow
We assumed for now that macro-mixing would be achieved by designing one large orifice using the current rapid mix orifice design but with a lower energy dissipation rate of 700 mW/kg

## Slide 12: Micro-Mix Orifice Sheet
We started with the LFOM orifice diameters and worked our way up until the diameter would allow for at least 5 mm of spacing between orifices.
For all flow rates, D ~ 4 in.
Head loss ~ 2.3 cm
K ~ 2
Porosity ~ 44%

## Slide 13: Spacing Issues…
Spacing is very small relative to orifice diameter.
80 L/s plant D = 4 in, S = 0.05 in.
To increase S:D, we would need to lower our initial head loss assumption

## Slide 14: New Idea: Micro-Mix Gate

## Slide 15: Micro-Mix Gate
PVC or steel
Porosity = 50%
HL = 1.1 cm
Minor Losses = 1
No vena contracta
Calculate spacing needed to achieve 1000 mW/kg
Calculate diameter given geometry constraints
D ~ 1 cm
Notes: Because of the spacing issue, we analyzed a different option: creating a “micro-mix gate” with either PVC pipes or rebar to create slots through which micro-mixing would be achieved. Assuming a porosity of 0.5, Ain:Aout is 0.5 and Vin:Vout is 2, so the minor loss coefficient through the gate is effectively 1 and the headloss through the gate is about half the headloss through the orifice sheet. The lower minor losses through the plant would lower the size of the channel, assuming the same 5 cm headloss.

## Slide 16: Aluminum Rapid Mix Gate
Including vena contracta for rectangular bars
More expensive
Less material
D ~ 0.45 cm

## Slide 17: Future Work
Micro-mix: Orifice sheet or gate?
Micro-mix Gate: PVC, steel, aluminum?
Macro-mix design needs further investigation
Hopper design constraints may need reevaluation
LFOM sheet to sutro weir cut out possibility

## Slide 18: Low Flow Plant
Julia Morris

## Slide 19: Intro
Current design range = 6 L/s – 70 L/s
Want to be able to serve small communities
Need new design for entrance tank, flocculator, sedimentation tank, and filter
Need new layout

## Slide 20
Ferrocement Baffles
Pipe Spacer – Takes up 60% of Upflow Area
Plastic Baffle
Notes: H/S ratio is too high still…so add pipe obstacles to create more collision potential

## Slide 21: Low Flow Sed Tank

## Slide 22: Entrance Tank
Wider Last Channel

## Slide 24: LFSRSF
Inlet
Outlet
Backwash

## Slide 25: Future Work
Finish up details on filter
Placement of filters
System to carry water from sed tank to filter

## Slide 26: Flocculator Design Detail
Kelly Huang

## Slide 27: Flocculation Tank

## Slide 28: Side Views of Flocculation Tanks
6 Lps
25Lps
50Lps
Notes: - Not neccesary at lower flowrates, but adding it to al of designs

## Slide 29: Modules
Modules
Array of Modules in a channel

## Slide 30: Two Types of Modules
  Overlapping modules Non-Overlapping modules
Notes: Define modules
Two cases
Currently all use Non-Overlapping modules so only N-O was modified

## Slide 31: AC Flocculator Code

## Slide 32
modified existing origin
shortened length of pipe
(elbow radius/tee length + 2*ND)

## Slide 33
tees and elbows were drawn using the same origin as the respective pipes

## Slide 34
Draw vertical pipes
(difference between z-coordinates)
- (elbow radius)
- (half of tee length)
________________________________
vertical pipe length

## Slide 35: Result (25 Lps)

## Slide 36: Future Work
Overlapping Case

## Slide 37: Materials List
Annie Ding
05/11/13

## Slide 38: Purpose
Calculate the amount and cost of materials needed to build a design requested from the server.
Useful for cities looking into getting a plant and construction teams.

## Slide 39: Materials
Hydraulic design materials:
Pipes
Pipe ﬁttings
Sheets for ﬂocculator baﬄes
Sedimentation plate settlers
Chemical dose controller pieces
Structural design materials include but are not limited to:
Brick
Rebar
Cement for plant walls
River rock for entrance tank hoppers

## Slide 40: Optimizing Pipes
Overall outputs:
  Matrix with the number of lances (6.1m lengths of pipes sold in Honduras) of each pipe specification and nominal diameter needed to build plant.
  Matrix with the lengths we can cut out of individual lances

## Slide 41: Accomplishments
Separated entire PipeMatrix into smaller matrices by nominal diameter (ND) and pipe schedule (EN)
Started code on cutting optimization

## Slide 42: Pipe Matrix Separation
Original pipe matrix
  Length
  Nominal Diameter (ND)
  Pipe schedule (EN)
  Number of times arrayed (N)

## Slide 43: Pipe Matrix Separation
PipeMatrix separated into Long and Short

## Slide 44: Pipe Matrix Separation
PipeMatrix separated by ND

## Slide 45: Pipe Matrix Separation
Matrices now separated by ND and EN

## Slide 46: Pipe Matrix Separation
Combine rows with the same length

## Slide 47: Pipe Matrix Separation
Separate the matrix with Long pipes into LanceMatrix and LeftoverMatrix

## Slide 48: For Pipes Longer than a Lance

## Slide 49: For Pipes Shorter than a Lance

## Slide 50: Getting as much out of a lance as possible (cutting stock problem)

## Slide 51: Future Work
Finish cutting optimization code
Edit pipe drawing code to output PipeMatrix
Test code to see if the numbers match up with numbers of pipes used in actual plants