## Slide 1: Tube Floc Experiments
Sophie Bernat
Team : Laura Floyd Alex O’Connell
Tami Chung Dali Sun

## Slide 2: Table of Contents
Introduction
Data analysis
Results
Conclusion

## Slide 3: Introduction
Goal:
  Understand flocculation in AguaClara plants
  Study the parameters that influence the results of flocculation.
    Residual turbidity
    Settling velocities

## Slide 4
FReTA Experimental Setup:

## Slide 5
Tube Flocculator

## Slide 6: Data Analysis
Essential tool used for analyzing data
    MathCad

## Slide 7: Data Analysis
MathCad
  Processes data and presents graphs plotting important information needed for data analysis
Main graphs we used for our experiment:
  Residual Turbidity Graph

## Slide 8: Residual Turbidity
Raw data: Turbidity vs. Sedimentation Velocity
Focusing on Residual Turbidity: Residual Turbidity vs. Sedimentation Velocity

## Slide 9: Residual Turbidity vs. Sedimentation Velocity
Alum Dose | Residual Turbidity
20 | 2.663
25 | 1.755
30 | 1.81
35 | 1.497
40 | 1.437
45 | 1.413
50 | 1.325
55 | 0.984
Notes: 100 NTU experiement @ 1st flocculator length.

## Slide 10: Varying Alum Dose and Flocculator Length
Goal: To determine the effect of alum dosage and flocculator length on tube flocculation.
Varied alum dosage (increasing by constant increments)
Applied the set alum dosages to three different flocculator lengths.

## Slide 11: Results
Effect of the alum dose on flocculation:
Chart: Residual Turbidity, 2796 cm
| 10.0 | 20.0 | 30.0 | 40.0 | 50.0 | 60.0 | 70.0 | 80.0
5 NTU | 1.742 | 1.006 | 0.761 | 0.653 | 0.712 | 0.627 | 0.633 | 0.655
100 NTU | 2.663 | 1.755 | 1.81 | 1.497 | 1.437 | 1.413 | 1.325 | 0.984
500 NTU | 6.397 | 3.901 | 3.123 | 3.486 | 2.566 | 2.635 | 2.786 | 2.297 | 2.467
Chart: Residual Turbidity, 8388 cm
| 0.0 | 1.5 | 2.25 | 3.375 | 5.06 | 7.59 | 11.39 | 17.09 | 25.63 | 38.44
5 NTU | 3.405 | 0.452 | 3.114 | 2.717 | 1.3 | 0.724 | 0.663 | 0.876 | 0.723 | 0.782
500 NTU | 5.464 | 3.949 | 3.073 | 3.598 | 3.252 | 2.967 | 2.873 | 3.206 | 3.18

## Slide 12: Results
Effect of length of the flocculator on residual turbidity:
Chart: 500 NTU
| 10.0 | 20.0 | 30.0 | 40.0 | 50.0 | 60.0 | 70.0 | 80.0 | 90.0
2796 cm | 6.397 | 3.901 | 3.123 | 3.486 | 2.566 | 2.635 | 2.786 | 2.297 | 2.467
8388 cm | 5.464 | 3.949 | 3.073 | 3.598 | 3.252 | 2.967 | 2.873 | 3.206 | 3.18

## Slide 13: Results
Effect of length of the flocculator on residual turbidity:
Chart: 500 NTU
| 10.0 | 20.0 | 30.0 | 40.0 | 50.0 | 60.0 | 70.0 | 80.0 | 90.0
2796 cm | 6.397 | 3.901 | 3.123 | 3.486 | 2.566 | 2.635 | 2.786 | 2.297 | 2.467
8388 cm | 5.464 | 3.949 | 3.073 | 3.598 | 3.252 | 2.967 | 2.873 | 3.206 | 3.18
Break up flocs
Steady state
  Floc size disribution constant

## Slide 14: Conclusions
Increasing alum dose improves flocculation initially but with diminishing returns as dose increases beyond a certain level

## Slide 15: In the Future
Complete our investigation of alum dose and flocculator length by collecting more data to fill in optimal alum dosages for the different influent turbidities
Run a test for FReTA
Begin investigating how pH affects flocculation

## Slide 16: Thank you
Question ?