## Slide 1: Sedimentation Tank Hydraulics
Anna Lee
Tiffany Tsang
Yiwen Ng

## Slide 2: Objectives
Understand the parameters that are important for floc blanket formation
Modify current sed tank geometry such that a floc blanket forms quickly and reliably

## Slide 3: Floc Blankets
Fluidized and highly concentrated bed of particles
Improves effluent performance by significantly enhancing particle removal
Reduce clean water waste from frequent draining of sed tank
Floc-water
interface
Notes: Floc blanket is a thick concentrated layer of particles that grows in size and density as it traps more and more particles.
Previous research has shown that the floc blanket can significantly enhance particle removal, thereby improving effluent performance. Picture shows floc-water interface with relatively less turbid water above the floc blanket. We want to create a floc blanket in the sed tank such that this interface is below the plate settlers.
The sed tank does not need to be drained out as often to clean out the sludge, because we want to build up the floc blanket. Can save clean water.

## Slide 4: Conditions for Formation
Floc re-suspension
  Sufficient jet velocity to scour settled flocs
  Settled flocs are directed towards upward jets
Notes: Flocs are always settling in the floc blanket, especially since upflow velocity is not uniform throughout the tank.
Nevertheless, a floc blanket can still be formed if there is adequate floc re-suspension.
The jet velocity is high enough to scour settled flocs
Settled flocs are directed towards the upward flowing jets to be resuspended

## Slide 5: Why no floc blanket now?
Inadequate floc resuspension
Tank geometry creates in dead zones and sludge formation
Circulation may disrupt the floc-water interface
Notes: Jets exiting the manifold are not strong enough to scour the flocs on the tank bottom
Geometry is such that dead zones form at the front and back ends of the tank. Dead zones are areas where settled flocs are not redirected towards jets that can resuspend them. This causes settled flocs to collect and form sludge at the corners. Dead zones are less likely to form in the middle portion of the tank because of the 60’ inclines which can direct flocs to the middle where the jets are located.
Circulation caused by the horizontal velocity component of the jets exiting the manifold can cause excessive turbulence at some parts of the floc blanket, diminish ability of blanket to catch flocs.

## Slide 6: Initial Design
Current Sedimentation tank design in Honduras
Use as control
Notes: 1. inlet manifold with orifices
2. inlet manifold with diffusers
3. no manifold, single jet
Our initial step: confirming the hypothesis we have regarding no formation of floc blanket
Problem
Dead zone: no resuspension
not large enough velocity to vertical scour velocity
3. Circular flow motion

## Slide 7: Proposed Design
Inserts & Diffusers
  Floc Re-suspension
  Reduce Dead Zones
Insert angles?
Vertical Scour Velocity?
Notes: 1. inlet manifold with orifices
2. inlet manifold with diffusers
3. no manifold, single jet
This is a good proposed design
However we have come to conclude that there are more critical parameters that we have not yet characterized.

## Slide 8: Single Jet
A single diffuser of the proposed design:
Diameter of diffuser so that energy dissipation rate 10 mW/kg is not exceeded
Height of diffuser above the tank floor chosen so that scouring velocity achieved for a reasonable coverage diameter: these variables depend on flow rate and diameter of diffuser
Notes: tiffany

## Slide 9: Single Jet
We can improve the height of the diffuser by assuming a Gaussian distribution of the flow through the jet:
Which means we can
experimentally determine v.scour
Design for spacing of orifices based on a chosen height
Preliminary Calculations:
Based on 2000 mL/min flow rate
v.scour predicted based on observed size of settled flocs (1 cm)

## Slide 10: Future Work
Study and learn about the controlling parameters using Matt's 2D apparatus (single jet model)
  Determine scour velocity and optimal angle of inclines
Design and construct a 3D tank to observe and measure floc blanket growth

## Slide 11: Questions?