## Slide 1: One valve control of a SRSF
The following slides illustrate the possibility of using a siphon tube to initiate backwash
The filter animation only shows how the siphon will work. It doesn’t yet show how the inlet and outlet manifolds will be controlled
The Filter Inlet and Outlet control boxes will be designed so that water level changes* during backwash will cause all of the manifold pipes to be hydraulically separated and thus no valves will be required to turn off the inlet or outlet pipes
Notes: *This will require a slight increase in the depth of the filter to accommodate a larger change in water levels between filtration and backwash

## Slide 2: Begin Filtration

## Slide 3: Begin Backwash
Notes: Need to analyze the beginning of the siphon right after the air pressure is equalized with atmospheric pressure. It appears that we may need the height of water above the top of the siphon tube to equal the depth of submergence of the end of the siphon to initiate flow through the siphon

## Slide 4: End Backwash

## Slide 5: Filter inlet control box
Max water level at end of filtration cycle
Backed up to within 10 cm of sed tank exit weir height
Water level at beginning of filtration cycle
Max water level during backwash
1
2
3
4
Inlet to bottom of filter (used for backwash)
Inlet to lower middle of filter
Inlet to upper middle of filter
Inlet to top of filter
No need to use plugs to shut off inlets to filter. The water lever during backwash is low enough that the 3 upper inlets are effectively isolated.
Max filter head loss (30 cm)
Notes: At the end of backwash the water level in this control box will gradually rise and water will begin flow in turn into each of the inlets. Pipe 1 must be sized large enough so that it can contain a free fall of water during backwash or the box must be deep enough to guarantee that the water level is inside the box during backwash.

## Slide 6: Filter outlet control box
1
2
3
Outlet from bottom of filter
Outlet from middle of filter
Outlet from top of filter
Filter to waste drain line
Filter to clear well
4
5
Pipe plug that can be used to shut off flow to waste so that flow goes to clear well.
During backwash the water level is lower than the base of this channel so that water can not flow through any of these outlets. This means that the base of this channel must be at most 20 cm below the max water level during backwash (shown in previous slide).
The outlet pipes will not need to be closed off during backwash because the water level during backwash will be below the channel bottom effectively blocking flow between pipes.
Notes: The weir configuration will not be as shown. It will be a single long weir that runs the length of this channel dividing it into two. The two exit pipes (4 and 5) will be on the downstream side of the weir.