## Slide 1: Fabrication
Harrison Gill, Julie Silva, Michael Walsh

## Slide 2
Alum Dose Distribution
Revision for high flow dosing

## Slide 3: Scope of project
Critical in inducing efficient flocculation.
Dosage range: 10-60 mg/L
Proper portion of alum to influent
Manually adjustable flow through a lateral pipe.

## Slide 4: 100 HOLES of UNIFORMITY

## Slide 5: Machining…
Mill for precision
(2mm spacing)
3/64th inch drill bit
Starter drill bit required
to avoid wabble

## Slide 6: With holes completed needed a way to adjust how many are open
IDEAS:
PVC disks
Tape PVC dowel
Rubber gasket
Lathe PVC rod to exact diameter
Obstacles:
Non-uniform inner diameter
Water tight seal needed

## Slide 7: PVC disks compressing rubber gasket
Started machining… realized it was not as easy to make really small plates.
Moved on…

## Slide 8: Electrical Tape to correct diameter
Simple design – Use PVC
rod and enlarge with tape
to fit inner diameter
df
Ran into issues:
Leaks through
Tape is easily deformed
Gets stuck / caught on holes

## Slide 9: Washer Gasket Combination

## Slide 10: Bolt Assembly
Washers replace PVC disks with ease
Bolt conveniently tightens assembly into rod

## Slide 11: Creating the Gasket
Lathe PVC pipe of same inner diameter into “cookie cutter”
Apply pressure/spin into sheet rubber to create cut.
Cut out inner hole
to quarter inch
for bolt

## Slide 12: Current Design
Rubber gasket and washers on PVC rod.
Essentially air tight
Easy to assemble
Toughest machining:
  Requires tapping PVC rod with 1/4th – 20 thread
Possibility of doubling gasket width for extra seal
Still a work in progress!

## Slide 13: Pipe Stub Valve
Pipe stub valves

## Slide 14: Finished Valve
The final designs incorporates elements from the flat plate design and pipe stub design.
  Includes a very short pipe stub to guide the valve
  Flat plate and gasket assembly to seal on the coupling

## Slide 15: Plate Valve

## Slide 16: Hydrometer
Hydrometer Fabrication Method
Find a container that will be bouyant even supporting weight.
Attach a thin rod to the cap, make watertight.
Create a solution with a 1.0114 specific gravity.
Add weights until the container/"chamber" is submerged.
Mark this line on the rod. This is optimal concentration.

## Slide 17: Hydrometer

## Slide 18: Jet Reverser
Current designs use a drain channel and cover
Moving to a drain pipe which allows jet reverser to be integrated with the drain system
Methods to connect the jet reverser to the drain pipe.

## Slide 19: Jet Reverser