## Slide 1: Stock Tank Mixing
Alexandra Cheng
Apoorv Gupta

## Slide 2: Semester Goals
Design a new stock solution mixing system
Perform small-scale testing and assess inefficiencies to make appropriate adjustments
Provide design blueprint for full-size system

## Slide 3: Bucket Mixer Design
Bucket with 16 0.156” diameter holes
Base projected area approximately 33% of tank base area
Drain dense solution at the top of the free surface

## Slide 4: Plate Mixer Design
1” PVC plate, 33% of tank base area
Create jets and turbulence to encourage mixing
Lift mixer within the height of the dense solution and plunge up and down

## Slide 5: Result Comparison: Bucket vs. Plate

## Slide 6: Plate Test Demo

## Slide 7: Base-Level Water Injection
Inject water into the bottom of the stock tank containing dense solution
H = 2.1 cm due to injection, 1.9 cm from water transport

## Slide 8: Water Injection Results

## Slide 9: Water Injection Full-Scale Schematic
Head due to injection set at 50 cm
Total Head 54.3 cm (difference from original RAM pump setup)
Required orifice size = 2.1 mm diameter
Best procedure:
  30% of water + stirred in coagulant
  Remaining 70% of water injected at base level
  Complete mixing using the plate mixer

## Slide 10: Future Work
Implement mixing system in San Nicolas and make necessary adjustments
Add mixer and injection process to the design code

## Slide 11: Questions