## Slide 1: Ram Pump
Ariel Seidner, Ruben Ghijsen, Kelly Huang

## Slide 2: Purpose for AguaClara
To provide plant with clean water for coagulant mixing and bathrooms
San Nicolas, Honduras
Plant
Distribution Tank
Ram Pump
Storage Tanks
7m
1.4 m

## Slide 3: Model 1 Schematic

## Slide 4: Simulating Honduras
Overview
Air column
Schematic
Recycling System

## Slide 5: Constant Head loss
Complicated to equalize
Relative stability maintained

## Slide 6: Decrease in Headloss
Slight decrease from fittings or absorption by water (air solubility)
Chart: Headloss (close-up)
Chart: Headloss (AC Model#2 Trial 2)
Notes: This would be to explain the slight decrease in headloss that we see after we run the apparatus for a while….

## Slide 7: AguaClara Model 1
Installed sensors and connected to PC
  pressure spikes
  head loss

## Slide 8: Initial Understandings
Valve Opens
Valve Closes

## Slide 9: Spring versus Swing
Comparison of the two setups
Spring
Swing

## Slide 10: Air Chamber
Effects of air added to the air chamber inconclusive – partially due to head loss system.
Theoretical Max Volume/Cycle
=123mL
Air volume in Chamber (20-50)x
Between 2.46L and 6.15L

## Slide 11: The Davey Ram Pump
Model: RIFE Davey Ram Pump
Same components
Order
Closeness
Entry/Exit pipe

## Slide 12: What we learned
Model 1
Head loss (cm) | Delivery Rate (mL/s) | Power (W)
476.21 | 17.56 | 0.8203
655.74 | 12.48 | 0.8028
722.82 | 16.70 (sp) | 1.184
738.35 | 14.11 (sp) | 1.022
766.73 | 6.187 | 0.4653
Head loss (cm) | Delivery Rate (mL/s) | Power (W)
529.22 | 25.84 | 1.342
602.84 | 26.81 | 1.586
679.21 | 24.67 | 1.643
733.54 | 20.18 | 1.452
Commercial Pump

## Slide 13: AguaClara Model 2
Why is it better?
How does it work?
What are the major changes?

## Slide 14
Air Chamber
Waste Valve
Check Valve
Delivery Pipe
Drive Pipe

## Slide 15: Final Deliverables
Position of components
The success of AguaClara Model 2 – improved flowrate
Head Loss (cm) | Delivery Rate (mL/s) | Power(W)
548 | 28.8 | 1.55
Head Loss (cm) | Delivery Rate (mL/s) | Power(W)
529 | 25.8 | 1.34
Model 2
Commercial Pump

## Slide 16: Future Work
Try different waste valve designs
Change set-up
Size of Air Chamber (determine efficacy)
  Entry and exit pipes
measure and adjust air inside
study commercial ram pump
Flow rate measuring device
Mathematical Model

## Slide 17: Questions?