## Slide 1: Ram Pump
Abby Brown, Annie Ding,
Pablo Nistal, Kadambari Suri

## Slide 2: What is a ram pump?
= ?????
Notes: Abby Where used in AguaClara plants? -San Nicolas has one to supply stock tanks with clean water for making chemical solutions
Potential future usefulness of the pump- expansion to India

## Slide 3: Why do we want to use a ram pump?
Notes: This is what we want to prevent - Abby

## Slide 4: Set-up: In the Plant
Storage Tanks
AguaClara Plant
Distribution
Ram Pump
Waste water
Pumped water
Effluent
Notes: Abby

## Slide 5: Set-up: In the Plant
Notes: 12:40 into the video https://www.youtube.com/watch?v=KjRkhhcRi4U - Bari

## Slide 6: Set-up: In the Lab
Notes: Bari - explain flow through the system

## Slide 7: Drive Pipe
Shorter distance between components
Longer distance between components
Notes: Pablo - Two different drive pipes, one shorter and another one longer in order to see how the different distances between components work. Theoretically, the shorter one should work better.

## Slide 8: Waste Valve
1” vs ¾” Brass
Notes: Pablo - Two different waste valves in order to check the impact of the size in the performance of the pump. However, different systems inside (ball vs plate) make this comparison irrelevant*

## Slide 9: Air Chamber
4 sizes of PVC:
9”, 12”, 15”, 25”
Accommodates
the different pressures.
Notes: Pablo - The size of the air chamber depends on the water that we expect to go into it per cycle. This amount has to be small enough in comparison with the air so that the variation of pressure in the air per cycle is unnoticeable (continuous outlet)

## Slide 10: Tee System
Notes: Pablo

## Slide 11: Encountered Problems
Head loss system
Notes: Annie

## Slide 12: Encountered Problems
Waste Valve Wear
Notes: Annie

## Slide 13: Results
Q=ESF/L
Q = outflow rate
E = energy efficiency
S = inflow rate
F/L = ratio between height to source and height to destination, both from the ram pump.
Notes: everyone - First, is the assumption of linear relation correct? Yes it is! Then keep going for the different arrangements.

## Slide 14: Results
S2 = Long drive pipe
A3 = 9’’ Air chamber
W# = #x50g weight
Notes: everyone - Now that we know that the assumption of linear relation is correct, lets try one system. How does it behave? Less weight = better performance but lower reliability. Optimal 4W?

## Slide 15: Results
Notes: everyone - Once we have seen the behavior in one, lets compare them! Outflow is continuous for all of them and performance is slightly better in the bigger ones.

## Slide 16: Results
Notes: everyone - Tee system, did it make any improvement? (not statistically significant)

## Slide 17: Problems
Losing energy from the 90 bend
+
Potential valve leakage
+
Short cycle time.
Prevents us from having an optimal amount of water going through each cycle.
Notes: Bari

## Slide 18: Future Work
Change the orientation
Notes: Abby

## Slide 19: Future Work
What?
Notes: Pablo - What do we want? Get rid of all the unnecessary parts (elbows, connections…)

## Slide 20: Future Work
How?
Notes: Pablo - How? Is this feasible? Due to the shortening, cycle time is going to be reduced drastically - We have to minimize cycle losses - Reduce distance between components and accommodate sizes to the new rates.

## Slide 21: Future Work
Experimentation with vertical valve
System works!
But...very low flow rate
How do we fix it?
Notes: Annie

## Slide 22: Future Work
Bring the spring valve and swing valve closer.
→ Weld them such that they are connected.
Manipulate the spring constant.
→ Order springs with varying spring constants in order to enable experimentation for the ideal spring.
Notes: Bari

## Slide 23: Questions/Comments/ Suggestions?
Notes: everyone