## Slide 1: Venturi and Low Flow Flocculator
Ryan Anthony, Elyssa Dixon and Zac Edwards

## Slide 2: The Venturi: Investigating the Potential of Floc Recycle
What is Floc Recycle? | Return flocs from the floc blanket in the sedimentation tank to the flocculator
Why Floc Recycle? | Recycling improves efficiency of flocculator: decrease length of flocculator, lower costs
How Can We Floc Recycle? | Integrate a Venturi into the Rapid Mix Pipe
Brief Background
Put on your helmet,
This will be a wild ride,
Down Venturi Lane.

## Slide 3: How Will A Venturi Solve the Problem?
Notes: Zac – Describe diagram

## Slide 4: Key Equations
1. Recycle Flow Rate
2. Difference in Head
3. Total Head Loss
4. Pressure in Throat
Notes: Elyssa – smaller throat = increase in head loss through venturi, which is why we want to find the maximum throat diameter that will still provided enough difference in head to transport flocs.

## Slide 5: The Program
12 L/s Plant With Working Venturi
VARIABLE | DESCRIPTION | VALUE
dEntranceNominal | Nominal Diameter of Rapid Mix Pipe | 8 in
dThroat | Diameter of Throat in Venturi | 9.86 cm
DiameterRatio | Ratio of Entrance Pipe Diameter to Venturi Throat Diameter | 2.055
LVenturi | Length of Venturi | 1.046
Expansion | Angle of Expansion in Venturi | 7
Contraction | Angle of Contraction in Venturi | 60
LRecycle | Length of the Recycle Pipe | 8.83 m
dRecycle | Diameter of the Recycle Pipe | 3 in
Coding this program
Was a formidable task,
But we did prevail.
Notes: Zac - transition

## Slide 6: Visual Representation
d.Recycle = 3 in
L.Venturi = 1.05 m
L.Throat = 6 in
d.EntranceNom = 8 in
α.Expansion = 7°
α.Contraction = 60°
See our venturi,
Flamboyant and majestic:
It recycles flocs.
d.Throat = 3.88 in
Notes: Zac

## Slide 7: Intermission
Put our flocs curbside
Place them next to the trash can
They are recycled.
3 Liters Per Second
Needs better water treatment
People are thirsty.
We make venturis,
But if we get frustrated,
We look at ram pumps.
Notes: Zac

## Slide 8: Low Flow Flocculator
Obstructions in a Pipe
  Remove geometric constraints
  Baffles and Balls
Utilize current AguaClara knowledge
In plants with low flows
Flocculation is no good
We shall overcome
Notes: Elyssa

## Slide 9: Assumptions
H/S = 4
Collision Potential
Efficiency = 0.95
eMax = 10 mW/kg
Energy Dissipation
Uniformity = 2
eAvg = 5 mW/kg
We made assumptions.
They were real big assumptions.
But do they hold true?
Notes: Elyssa

## Slide 10: Baffles
Current plants maintain cross-sectional area of flow
Modify to pipe
  Distance Correlation
  Area Correlation
Dimensions
  H = Pipe Diameter
  S = Spacing
  W = Average Chord Length
What’s our favorite word?
Flocculation. Flocculate.
Floc. Floc. Floc. Floc. Floc.

## Slide 11: Baffles – Distance Correlation
Maintain Spacing
  Current AguaClara Flocculators
  Loss due to flow expansion
Our Balls and Baffles
Could revamp AguaClara
Can they really work?
Notes: Elyssa

## Slide 12: Baffles – Area Correlation
Maintain Area
  Eliminate loss due to flow expansion
Notes: Elyssa

## Slide 13: Balls in a Pipe
Notes: Zac
H = d.Floc

## Slide 14: Balls in a Pipe
“Dead Zone”
LBalls
dJet
rBall
LBalls is a geometric property based on the expansion of jets
Notes: Zac
S=L.Balls

## Slide 15: Summary and Comparison for 3 L/s
Both options can work.
Only one can be the best.
We find it baffling.
Notes: Zac

## Slide 16: Baffle Spacing Comparison
Distance Correlation
Area Correlation
8.9 cm
12.6 cm
36 cm
36 cm
Top of Baffle
Top of Baffle
Notes: Elyssa

## Slide 17: Uncertainty
Sensitivity to Assumptions
Baffles
Balls
  Assumptions:
    ae=2
    eMax=10 mW/kg
  Recalculation Yields:
    ae=10
    eMax=20 mW/kg
If Monroe were king,
All the water would be clean.
Instead, we do work.
Notes: Zac
Baffles – ensure that calculations are current for converting AguaClara stuff into pipes

## Slide 18: Future Work
Fix Balls
Price comparison
Constructability
Method to observe flocculation
Prototype to compare to calculated values
Low Flow Flocculator
Venturi
Notes: Elyssa
BUILD

## Slide 19: Questions?
I like burritos.
I think most people do too.
Let’s make clean water.
We provide water.
We might also save the world.
We do what we can.
Would you like to have
A refreshing glass of mud?
I prefer water.
We stay up all night
Writing MathCad documents
And then we revise
Venturis are cool
We wanted to construct one
‘Twas not meant to be