## Slide 1: Floc Sed Optimization Team
Summer Teach-In
July 25th, 2012
Mary John
Kaditya Naidu
Elizabeth Henderson

## Slide 2: Challenges
Run tests varying the following conditions: turbidity, flocculator length, alum dose, flow rate, capture velocity and rate of floc recycle flow
Collect and format data in Mathcad
Maintain floc blanket throughout experiments
Ultimate goal: best performance at lowest cost
Notes: -

## Slide 6: Problems Encountered
Cleaning out the flocculator
Flooding our working space
Calibrating the pump (old-fashioned way)
Nested codes on Mathcad (Slow in rendering results)

## Slide 7: Remember
What happens in the lab stays in the lab!

## Slide 8: Analysis
20 m flocculator control
20 m flocculator with floc blanket

## Slide 9
Influent Turbidity
Effluent Turbidity
Notes: Turbidity is the cloudiness or haziness of a fluid caused by individual particles (suspended solids) that are generally invisible to the naked eye, similar to smoke in air. The measurement of turbidity is a key test of water quality.

## Slide 10
15 m flocculator control
15 m flocculator with floc blanket

## Slide 11: Summary of Results
Experiment | Influent Turbidity | Effluent Turbidity | pC* (State 3-35mg/L)
21: 20m flocculator control | 200 | 90 | 0.45
22: 20m flocculator with floc blanket | 200 | 4 | 1.55
23: 15 m Flocculator control | 200 | 8-9 | 1.45
24: 15 Flocculator with floc blanket | 200 | 0.5 | 2.4

## Slide 12: Results
Floc blankets work!!
Water is less turbid after passing through a floc blanket
Lower alum doses yield similar results as higher alum doses
Possible to reduce flocculator length and alum dose
Notes: -

## Slide 13: Future Work
Determining the smallest flocculator length that will still form a floc blanket
Continuing to change variables including flow rate, capture velocity and rate of floc recycle flow
Use this data to determine optimal performance at lowest cost