## Slide 1: Turbulent Flocculator
Ana Oliveira, Felice Chan, Jonathan Christensen, and Stephen Jacobs
Fall 2013

## Slide 2: Goals
Designing, building and testing a lab scale turbulent tube flocculator.
  Raw water turbidity, coagulant, and flow control
  Measure effluent turbidity
Notes:   Turbulent regions on the flow through the flocculator
  The importance of understanding the prior design from the Summer team

## Slide 3: Design from Summer 2013
Stacked coiled tube
Rods to create constrictions for turbulence
Diameter = .614 m (about 2 feet)
30 coils high
Constricted height = 1.464m (about 4.8 ft)
General Design from Summer 2013

## Slide 4: AutoCAD drawings
Notes:   Calculation of the length, the diameter, and the number of coils of the flocculator
  Adding important equipment: clay stock, turbidimeters, pumps, stirrers, temperature and pressure

## Slide 5: Materials To Purchase
Thin Walled Metal Tubing
Solenoid Valve
Clamping Materials (Steel Bar and PVC)
Head Tank
Fittings for flocculator
Bulk Head Fitting

## Slide 6: Thin Walled Metal Tubing
Because the flexible tubing came in four separate pieces we need a way to connect them.
ID:1.25”
Flexible Tubing
Rigid Tubing
Notes: 1. Drawing from Summer 2013 Powerpoint

## Slide 7: Solenoid Valve Testing
The team measured from the flow from the sink and from the solenoid valves in the lab.
The flow from the existing solenoid valves were insufficient.
The existing valves in the lab have an orifice diameter of 3mm
  Qcold.tap = 315 mL/s
  Qhot.tap = 295.1 mL/s
  Qvalve = 59.2 mL/s

## Slide 8: New Solenoid Valve
Minimum Orifice Diameter = 3.456mm (0.136 in)
Actual Orifice Diameter = 0.156 in
Qvalve = 130 mL/s
Orifice Diameter= 0.156 in
Pipe Diameter= 0.25 in
Notes: Orifice Diameter is 5/32”
Pipe Diameter is .25”
Voltage: 120 AC
Purchased from Grainger
Talk about the thing that Paul made for us

## Slide 9: Clamping Materials
Need long round tubes to create constrictions
  Approximate ID of tube should be between 1” – 1.5”
  The deformation of the tube must be minimal.
Need a way to create a frame or base so the flocculator can stand on its own.

## Slide 10: Beam Deformation Calculations
Max deformation for simply supported uniformly distributed load
Force was taken to be hydrostatic force from water and elastic force from tubing

## Slide 11: Clamping Materials
Purchased Schedule 40 1-inch PVC and a steel bar.
The steel bar will fit inside the PVC to create the rigidity that we need.
1/4" Thick, 1" Width
6’ Length

## Slide 12: Proposed Design
Drill holes in Plywood Base and place PVC tubes in the holes.

## Slide 13: Rapid Mix
2.4 cm

## Slide 14: Head Loss

## Slide 15: Future Work
Finalize design and purchase the rest of the materials.
Construct the flocculator.
Set up process controller.
Run experiments!

## Slide 16: Questions?