## Slide 1: Stacked Rapid Sand (StaRS) Filter Theory
Theresa Chu
Alexandra Scwhab
Guillermo Garcia

## Slide 2: Stacked Rapid Sand Filters
Stacked Rapid Sand (StaRS) Filter/Filtration
AguaClara invention
Water enters the filter through slotted pipes
Sand captures colloids
Entirely gravity-powered water filtration

## Slide 3: Purpose
Confirm data from Spring 2014
  Very variable
Test head loss across mesh

## Slide 4: Slotted Pipes
Is there head loss across the copper mesh?
  Openings: 0.23 mm
Slotted pipes
  Openings: 0.2 mm
  Clogging
Hypothesis:
Head loss across copper mesh
Head loss across slotted pipes
͠

## Slide 5: Experimental Apparatus

## Slide 6: Experimental Apparatus

## Slide 7: Methods
Conditions:
  Influent Turbidity: 5 NTU
  PACl dosages: 0.2 mg/L; 1.1 mg/L; 2.0 mg/L
  Run time: 12 hours
  Sieve sand between No. 30 and 40 (Factor: 1.5)
Cleaning copper tubing/mesh:
  Physical: scrub mesh
  Chemical: soak in acetic acid

## Slide 8: Mesh Only Head Loss
PACl dosage: 2.0 mg/L
Influent Turbidity: variable

## Slide 9: Mesh Only Head Loss
PACl dosage: 2.0mg/L
Influent Turbidity: 5 NTU

## Slide 10: Mesh Only Head Loss
PACl dosage: 1.1 mg/L
Influent Turbidity: 5 NTU

## Slide 11: Mesh Only Head Loss
PACl dosage: 0.2 mg/L
Influent Turbidity: 5 NTU

## Slide 12: Conclusions
Best performance expected: sand sieved
Head loss increases with coagulant dosage
Head loss on the mesh
  Negligible ( hL < 5 cm)
  Significant (hL > 30 cm)
Slotted pipe/Mesh alternative
Notes: Mesh head loss ratio: over 1/50

## Slide 13: Future Work
Alternative to copper mesh
Larger openings
  Mesh: 0.23 mm
  Sand: 0.400 mm to 0.595 mm
Non-corrosive metal

## Slide 14: Future Work
Alternative to slotted pipes
  Reduce clogging, head loss
U-design
  Sand does not revert backwards
http://www.analyzemath.com/Geometry/3D_shapes_problems.html

## Slide 15: Questions?