## Slide 1: Stacked Rapid Sand (StaRS) Filter Theory
Theresa Chu
Nick Coyle
Alex Schwab

## Slide 2: Stacked Rapid Sand Filters
Stacked Rapid Sand (StaRS) Filter/Filtration
Invented by AguaClara and used in newer plants
Water enters the filter through slotted pipes
Sand captures colloids
Allows for entirely gravity-powered water filtration

## Slide 3: Purpose
StaRS Filter Theory
  Mathematical model
Fall 2014
  Head loss across copper mesh
  Results are inconsistent
Spring 2015
  Head loss across slotted pipes

## Slide 4: Slotted Pipes
0.2 mm wide
Clogging
  Flocs clog openings
  Sand caught in slots
  Biological growth
Expensive to fabricate

## Slide 5: Hypothesis
Head Loss
Clogging due to flocs
Coagulant-clay ratio
  Optimal conditions
  for flocs

## Slide 6: Failure Points and Clogging
Head loss
  StaRS Filters: 50 cm allotted
  Slotted Pipes: 5 cm
Clogging
  Total clogging of pipe not likely
  Shear force of water

## Slide 7: Methods
Experimental Apparatus
PACl Clogging Rapid Mix Pipe

## Slide 8: Methods
Biological Growth
Pre-Experiment Cleaning
Rapid Mix Pipe Clogging
Six roller peristaltic pump

## Slide 9: Experiments
Influent Turbidity
  <5 or 500 NTU
PACl
  10.6, 26.5, 60.8 mg/L Al
Runtime: 6 hours
Apparatus Design:
  Filter flow rate: 0.8 L/s
  Flow through slot: 1.1 mL/s
  Flow through apparatus: 6 mL/s

## Slide 10: PACl Only
0 hours
2 hours
1 hour
6 hours
5 hours
4 hours
3 hours

## Slide 11: Clay Only
0 hours
2 hours
1 hour
6 hours
5 hours
4 hours
3 hours

## Slide 12: PACl and Clay
0 hours
2 hours
1 hour
6 hours
5 hours
4 hours
3 hours

## Slide 13: Observations
Clogged: Clay and PACl
Clean

## Slide 14: Observations: Unclogged

## Slide 15: Observations - Clogged

## Slide 16: Clay Only
Influent Turbidity: 500 NTU

## Slide 17: PACl Only

## Slide 18: PACl and Clay
PACl: 26.5 mg/L Al
Influent Turbidity: 500 NTU

## Slide 19: PACl and Clay
PACl: 26.5 mg/L Al
Influent Turbidity: 500 NTU

## Slide 20: PACl and Clay
PACl: 26.5 mg/L Al
Influent Turbidity: 500 NTU

## Slide 21: PACl and Clay
PACl: 26.5 mg/L Al
Influent Turbidity: 500 NTU
Need flocs to cause head loss

## Slide 22: Conclusions
Slotted pipes clog
  Presence of flocs (clay and PACl ratio)
  Amount of coagulant dosage
Head loss
  High PACl dosage (15 cm)
  High PACl dosage and influent turbidity (30 cm)
Replace slotted pipes

## Slide 23: Future Work
Better characterize clogging conditions with consistent PACl dosage
  PACl only
  PACl and Clay only
Design new injection system for StaRS Filters
Create mathematical model of colloid capture in sand

## Slide 24: Questions?