## Slide 1: Surface vs. Subsurface Injection for Sand Filter
Summer 2013
Theresa Chu
Kelly Huang
Vikram Kejariwal
Tanya Peifer

## Slide 2: Goals for Summer 2013
Determine clogging conditions
Whether backwash is sufficient in unclogging the filter

## Slide 3: Apparatus

## Slide 4: Hypothesis
Clogging will most likely occur at
  low filter velocity
  high PAC dosage
Backwashing will require more effort at higher PAC dosages

## Slide 5: Current Research
Clay dosage (influent NTU)
  Constant at 100 mg/L
  Also testing no clay/just PAC
Filter Velocity
  0.916 mm/s – 1.833mm/s
  Recalculated (.48-.722 mm/s)
PAC dosage
  5 mg/L – 80 mg/L
Run Time
  Indefinite
Notes: Filter velocity = backwash velocity /6 (backwash velocity is typically 11 mm/s)

## Slide 6: Head Loss Analysis
Chart: Subsurface Head Loss vs. Time (Velocity = 0.722 mm/s)

## Slide 7: Head loss Analysis
Chart: Surface Head Loss vs. Time (Velocity = 0.722 mm/s)

## Slide 8: Turbidity over Time PAC 60 1.83mm/s

## Slide 9: Conclusions
PAC dosage directly effects Head loss but a clear trend has yet to be determined
Subsurface clogs faster than Surface
Subsurface is easier to backwash than Surface
Before subsurface clogs it has lower effluent turbidity than surface

## Slide 10: Future Work
Complete range of experiments to determine when clogging occurs
Construct a model to predict if clogging will occur