## Slide 1: Surface vs. Subsurface Injection for Sand Filter
Summer 2013
Theresa Chu
Kelly Huang
Vikram Kejariwal
Tanya Peifer

## Slide 2: Background
Subsurface injection – represents stacked rapid sand filter (SRSF)
Surface injection – represents conventional downflow rapid sand filter
Subsurface
Water
Injection
Surface Water Injection

## Slide 3: Goals for Summer 2013
Determine clogging conditions
Whether backwash is sufficient in unclogging the filter

## Slide 4: Definitions
Head Loss
Clogging
  Surface: head loss increases exponentially
  Subsurface: head loss is 1.4 to 1.6 times sand depth (or greater than 40 cm = ineffective)

## Slide 5: Apparatus

## Slide 6: Variables
Independent
  PAC dosage
  Filter Velocity
  Influent Turbidity
Dependent
  Head Loss
  Effluent Turbidity
Qualitative observations
  Backwash (videos)
  Clay build-up

## Slide 7: Hypothesis
Clogging will most likely occur at
  low filter velocity
  high PAC dosage
Backwashing will require more effort at higher PAC dosages

## Slide 8: First 50 experiments

## Slide 9: Head Loss vs. PAC Dosage

## Slide 10: Head Loss vs. Velocity
Chart: Head Loss vs. Velocity
| 0.45450000000000002 | 0.75670000000000004 | 0.90900000000000003 | 1.3640000000000001 | 1.5149999999999999 | 1.8180000000000001 | 2.2730000000000001 | 2.4239999999999999 | 3.03 | 3.3330000000000002 | 3.7879999999999998 | 4.5449999999999999 | 5.0149999999999997 | 6.0609999999999999 | 7.5759999999999996 | 9.0909999999999993 | 10.606
Max Head Loss Col 1 Surface | 2.1829 | 7.4497 | 24.4295 | 15.4063 | 17.3084 | 17.3724 | 71.4694 | 25.627 | 17.8041 | 45.5574 | 47.8259
Max Head Loss Col 2 Subsurface | 1.4258 | 6.0855 | 4.9739 | 14.5364 | 10.4533 | 14.788 | 36.3699 | 85.3584 | 22.9117 | 17.4699 | 62.2503 | 29.4808

## Slide 11: Head Loss Over Time
Chart: Time (s)

## Slide 12: Problems & Solutions
Only ran for 2 hours; no clogging occurred
Technical difficulties
  Pressure sensors
  Turbidimeter condensation
  Pump calibrations

## Slide 13: Problems & Solutions
  Clay buildup in dosing tube
  Inconsistent influent NTU (caused by settling clay in flow accumulators)

## Slide 14: Problems & Solutions
  Column leaking, sand escaping during backwash
air in columns

## Slide 15: Redesigned Experiments

## Slide 16: Current Research
Clay dosage (influent NTU)
  Constant at 100 mg/L
  Also testing no clay/just PAC
Filter Velocity
  0.916 mm/s – 1.833mm/s
PAC dosage
  5 mg/L – 80 mg/L
Run Time
  Indefinite
Notes: Filter velocity = backwash velocity /6 (backwash velocity is typically 11 mm/s)

## Slide 17: 1.52 mm/s 15mg/L PAC
Head Loss
Chart: Time (s)

## Slide 18: 1.52 mm/s 15mg/L PAC
Turbidity
Chart: Time (s)

## Slide 19: Future Work
Finish all proposed experiments
Find solution if backwashing isn’t sufficient
Analyze all data
Compile backwashing videos/ determine duration