## Slide 1: SRSF Theory
Theresa Chu
Tanya Peifer
Michelle Bowen

## Slide 2: What is SRSF?
Stacked Rapid Sand Filter/Filtration
Invented by AguaClara and used in newer plants
How is it different?
  Water enters the filter through embedded tubes
  Allows for entirely gravity-powered water filtration

## Slide 3: Why are we here?
Create a theoretical understanding of SRSF
Why?
This understanding can be used to optimize SRSF performance
How?
By conducting experiments while varying certain inputs and monitoring important outputs

## Slide 4: Challenges
Redesign the laboratory apparatus
Test and improve the turbidity feed system
Design a new system for coagulant dosing
Design and run experiments, varying important parameters
Begin developing a model for filter performance

## Slide 5: Designing the Apparatus
Construction parameters
  Number of layers required
    2 layer filter was the simplest option that modeled SRSF
  Height of filter
  Inlet and outlet tube dimensions and materials

## Slide 6: Redesigned Apparatus
One filter column
Models two layers of an SRSF, with one inlet and two outlets
Size considerations:
  Each filter layer is 20 cm
  Backwash expansion is approximately 30 %
Backwash space > .3*(40 cm)
Backwash space > 12 cm

## Slide 7: Inlet and Outlet Design
Ratio of inlet area and filter area needed to be similar to the ratio in AguaClara’s plants to achieve similar velocities
  = 0.04
  Inlet area = 0.04 * filter area
  Inlet area = tubing area – area occupied by mesh
  Velocity through filter: 1.8 mm/s
  Velocity through inlet: 45 mm/s

## Slide 8: Materials
Clear PVC
  Length: 60 cm.
  ID: 1 in.
Sand
  Diameter of 1 grain: 0.02 in.
Multipurpose copper tubing
  ID: 0.37 in.
Copper mesh
  Opening size: 0.009 in.
  Porosity: 30%

## Slide 9: Construction
Sealed end of filter
Drilled holes for inlet and outlet tubes
Threaded push-to-connect fittings were used to put the copper tubing inside the filter
  Fittings were drilled out to accommodate copper tubing
Copper tubing inserted halfway through column
Copper mesh welded on ends of copper tubing

## Slide 10: Testing the Apparatus
Is the influent turbidity constant?
Ran trials to measure turbidity
Must be within 10% of target value to be acceptable
Is the apparatus water tight?
Filled with water
Connected in system

## Slide 11: Current Issues
Influent turbidity varies
Coagulant loss on tubing
Old method: rapid mix chamber
  Clay settling out before reaching filter
  Coagulant coating the tubing and not the clay
Notes: Varying influent turbidity
-- while varying naturally in Honduras, in order to collect consistent data that tells us something, we need a constant influent turbidity
---also, by the time the turbid water gets to the filter, it is usually about 5 NTU

## Slide 12: Influent Turbidity: Sample Results

## Slide 13: Possible Solutions
For turbidity:
  PID system (uses Process Controller to measure levels of turbidity and add more or less clay stock depending on readings)
For coagulant loss:
  Direct injections (changed location)
  Larger contact chamber

## Slide 14: Turbidity with PID
Chart: Influent Turbidity vs. Time

## Slide 15: Future Work
Achieve constant influent turbidity
Continue running pilot experiments testing turbidity and addition of coagulant
Decide parameters for new experiments
Run experiments
Collect and analyze data
Develop model

## Slide 16: Experiment Parameters
Given:
  Constant Influent Turbidity (5 ± 0.5 NTU)
  Constant Flow Rate (0.929 mL/s)
Independent Variable:
  Coagulant Dosage
Dependent Variables:
  Effluent Turbidity
  Head Loss

## Slide 17: Developing A Model
Collect a group of performance curves using pC* and head loss
  pC* compares influent and effluent turbidities
Model filter performance
  Find pore storage volume as a function of coagulant dosage
  Predict head loss as a function of coagulant dose and mass of solids accumulated
Notes: 〖〖𝑝𝐶〗^∗ =−log〗⁡〖𝑒𝑓𝑓𝑙𝑢𝑒𝑛𝑡/𝑖𝑛𝑓𝑙𝑢𝑒𝑛𝑡〗

## Slide 18: Questions?