## Slide 1: Arsenic Team
Tanapong Jiarathanakul
Jason Koutoudis
Mingze Niu
Faculty Advisor: Professor Weber-Shirk
Student Advisor: Casey Garland

## Slide 2: Goal
Overall goal
  Design and improve AguaClara filtration unit to remove arsenic from influent
  Evaluate feasibility of implementation
This semester’s goal
  Fabricate a sand filtration unit
  Establish experimental procedure
  Improve arsenic detection method
  Measure arsenic removal

## Slide 3: Filter Design
Upflow sand filtration column
  Height of sand = 87 cm
Groundwater pump
  16 size tube
PACl pump
  13 size tube
Manometer to monitor head loss
Magnetic stirrer plate to mix PACl
Notes: Small quarter inch tube to bring the reference point down

## Slide 4: Experimental Procedure

## Slide 5: Preparation
Arsenic dilution in Groundwater
  Influent arsenic concentration is 100 ppb
PACl stock solution preparation
  100 mg/L PACl stock
  Equation for dilution factor
  Qtotal*Cin=QPACl*Cstock

## Slide 6: Preparation
Calibration of pumps
  Two pumps:
    PACl: size 13 tube,
    Groundwater: size 16 tube
  Evaluate flow rate of each pump at various rpm
  Calibration equations:
    PACl pump: rpm = 0.0717Q - 0.0417
    Groundwater pump: rpm = 1.2Q

## Slide 7: Experimental Steps
Initial Backwash
  Tap water
  Maximum flow rate of 100 rpm or 7.1 mm/s
  122% fluidization
  5 – 10 minutes

## Slide 8: Experimental Steps
Pre-treatment with PACl
  Pre-treated with 30 mg/L PACl in groundwater solution
  Total flow rate is 2.015 mm/s
  pH is between 6 – 7
  Stop pre-treatment when headloss increases to half of total height of the sand column (40 cm), from 80 to 120 cm, in 10 minutes
  Total mass injected is 2 mg

## Slide 9: Experimental Steps
Continuous Flow Experiment
  Samples are collected every 10 minutes
  Arsenic concentration in groundwater = 100 ppb
  PACl influent concentration = 1 mg/L
  Approach velocity= 1 mm/s
  Total flow rate= 11.76 mL/min
  Groundwater pump= 14 rpm = 11.642 mL/min
  PACl pump= 2.2 rpm= 0.118 mL/min

## Slide 10: Experimental Steps
Final backwash
  10 minutes at 100 rpm (7 mm/s) with groundwater
  Samples are collected every 1 minute for the first 5 minutes, then one more at 10 minutes

## Slide 11: Experimental Steps
Sample analysis
  GFAAS (Graphite Furnace Atomic Absorption Spectrometer) is calibrated prior to experiment
  Samples are analyzed during experiment for direct feedback
Notes: We want direct feedback to see if we are removing anything at all and changes over time.

## Slide 12: GFAAS Analysis

## Slide 13: Calibration Curve: 0 – 100 ppb
Chart: Calibration Curve 0 - 100 ppb
| 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
 | -0.00774 | 0.004408 | 0.012517 | 0.017426 | 0.037421 | 0.036901 | 0.039906 | 0.03215 | 0.050228 | 0.04346 | 0.052007 | -0.004213 | 0.005143 | 0.011142 | 0.024227 | 0.029631 | 0.045626 | 0.02867 | 0.041117 | 0.047066 | 0.048014 | 0.054967 | -0.003543 | 0.005107 | 0.0172 | 0.026278 | 0.03017 | 0.030381 | 0.036593 | 0.045703 | 0.050024 | 0.058548 | 0.050685
Notes: Set intercept at 0

## Slide 14: Arsenic Effluent Concentration
Chart: Arsenic Effluent Concentration Over Time
| 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 | 110 | 120 | 130 | 140
 | -4.1223 | -10.9773 | -1.4053 | -1.714 | -0.63428 | -12.4884 | -6.8098 | -6.9719 | -1.6752 | -8.7412 | -2.2039 | -8.0779 | 6.4242 | -8.5118 | -3.2587 | -6.9471 | -1.0338 | -0.95051 | -3.5036 | 2.9673 | -4.4501 | -2.7334 | -2.7285 | 5.7822 | -3.3437 | -6.9672 | -3.6019 | -9.1751 | 1.7845 | -3.7773 | 4.3655 | -1.5749 | -7.4422 | 3.5782 | -6.9979 | -2.2413 | -5.7111 | -4.8651 | -7.7402 | -4.7949 | 2.1616 | -3.8643
Co-treatment
No additional PACl
Notes: Direct feedback, decide to alter method when we saw no increasing trend
When changed, maintain superficial velocity

## Slide 15: Multiple Injection Method
Program Furnace Sequence

## Slide 16: Multiple Injection: Calibration Curve 0 – 10 ppb
Chart: Calibration Curve using Multiple Injection Method from 0 to 10 ppb
| 0 | 2 | 4 | 6 | 8 | 10 | 0 | 2 | 4 | 6 | 8 | 10 | 0 | 2 | 4 | 6 | 8 | 10
Sig | 0 | 0.005217 | 0.016486 | 0.023351 | 0.12294 | 0.14653 | 0 | 6.2e-05 | 0.018677 | 0.028235 | 0.12378 | 0.15506 | 0 | 0.010974 | 0.017935 | 0.033708 | 0.11764 | 0.11184

## Slide 17: As Effluent Concentration: Multiple Injection Method
Chart: Arsenic Concentration in Filter Effluent
| 20 | 40 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 20 | 40 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 20 | 40 | 60 | 90 | 100 | 110 | 120 | 130
 | 1.5184 | 1.7763 | 1.8055 | 1.8854 | 0.10698 | 1.9992 | 2.6125 | 3.568 | 8.3363 | 1.9656 | 1.3016 | 0.91912 | 1.3964 | 1.0118 | 1.2859 | 2.49 | 3.6549 | 8.27 | 1.4041 | 2.5038 | 1.8444 | 1.7214 | 1.4234 | 1.3688 | 3.8444 | 8.0052
Co-treatment
No additional PACl

## Slide 18: Calibration Curve: 0 – 50 ppb for Backwash Samples
Chart: Calibration Curve from 0 to 50 ppb
| 0 | 10 | 20 | 30 | 40 | 50 | 0 | 10 | 20 | 30 | 40 | 50 | 0 | 10 | 20 | 30 | 40 | 50
 | 0 | 0.064319 | 0.12629 | 0.18154 | 0.24214 | 0.29037 | 0 | 0.053715 | 0.1179 | 0.16269 | 0.23512 | 0.2882 | 0 | 0.068884 | 0.11583 | 0.18068 | 0.23893 | 0.2891

## Slide 19: As Effluent Concentration During Backwash
Chart: Arsenic Concentration in Filter Effluent during Backwash
| 1 | 2 | 3 | 4 | 5 | 10 | 1 | 2 | 3 | 4 | 5 | 10 | 1 | 2 | 3 | 4 | 5 | 10
 | 9.6902 | 11.8289 | 16.2916 | 18.2781 | 23.5533 | 17.9076 | 11.855 | 10.4805 | 14.2035 | 20.1171 | 21.6606 | 16.5039 | 11.6061 | 12.0175 | 13.1306 | 17.0804 | 22.1321 | 19.0361

## Slide 20: Data Analysis

## Slide 21: pC*
Chart: pC* of Arsenic Removal
| 20 | 40 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 20 | 40 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 20 | 40 | 60 | 90 | 100 | 110 | 120 | 130
 | 1.8186 | 1.7505 | 1.7434 | 1.7246 | 2.9707 | 1.6992 | 1.583 | 1.4476 | 1.079 | 1.7065 | 1.8855 | 2.0366 | 1.855 | 1.9949 | 1.8908 | 1.6038 | 1.4371 | 1.0825 | 1.8526 | 1.6014 | 1.7341 | 1.7641 | 1.8467 | 1.8637 | 1.4152 | 1.0966
Co-treatment
No additional PACl

## Slide 22: Is that so?
Chart: Percent Removal of Arsenic
| 20 | 40 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 20 | 40 | 60 | 80 | 90 | 100 | 110 | 120 | 130 | 20 | 40 | 60 | 90 | 100 | 110 | 120 | 130
 | 98.4816 | 98.2237 | 98.1945 | 98.1146 | 99.893 | 98.0008 | 97.3875 | 96.432 | 91.6637 | 98.0344 | 98.6984 | 99.0809 | 98.6036 | 98.9882 | 98.7141 | 97.51 | 96.3451 | 91.73 | 98.5959 | 97.4962 | 98.1556 | 98.2786 | 98.5766 | 98.6312 | 96.1556 | 91.9948
Co-treatment
No additional PACl

## Slide 23: Backwash
Chart: Arsenic Concentration in Filter Effluent during Backwash
| 1 | 2 | 3 | 4 | 5 | 10 | 1 | 2 | 3 | 4 | 5 | 10 | 1 | 2 | 3 | 4 | 5 | 10
 | 9.6902 | 11.8289 | 16.2916 | 18.2781 | 23.5533 | 17.9076 | 11.855 | 10.4805 | 14.2035 | 20.1171 | 21.6606 | 16.5039 | 11.6061 | 12.0175 | 13.1306 | 17.0804 | 22.1321 | 19.0361

## Slide 24: Future Work

## Slide 25: Establishing Base Line
Example

## Slide 26: Calibration Curve: Groundwater vs. HNO3
Arsenic standard
  0.2% nitric acid
    Prevent As from sticking to walls of container
Samples
  No nitric acid
  Groundwater ions

## Slide 27: Pre-treatment and Co-treatment
Compare the effectiveness of each method separately
  And derive insight into removal mechanism
Test different pretreatment methods
  Derive optimal method
  Evaluate method that could apply to stacked rapid sand filters, eg. treat at the end of the backwash cycle
Evaluate the effective dosage of co-treatment for 100 ppb As groundwater

## Slide 28: Removal efficiency rate in continuous flow
Better understand removal mechanism
Establish a stoichiometric relationship between coagulant dosage and effective Arsenic removal
  Run continuous flow experiment
  Observe the decrease in removal efficiency over time
Evaluate effect of pH

## Slide 29: Questions?

## Slide 30: Acknowledgements
Thank you:
Professor Lion
Professor Weber-Shirk
William Pennock
Casey Garland
Working harder to keep arsenic out of your water!