## Slide 1: Full Scale Floc Breakup
Team Members: David Buck and Meg Fitzgerald

## Slide 2: The Goal
Big Flocs are useless

## Slide 3: The Concept
Notes: Velocity Gradients cause shear

## Slide 4: Basic Design

## Slide 5: Design Procedure
Set Constraints
Target Floc Size and Energy Dissipation Rate
Optimal Number of Devices
Orifice Size and Porosity Design

## Slide 6: Constraints: What are the failure modes?
  Energy dissipation
  Head Loss
  Porosity
Break up Flocs
Overtops the baffles
Streamlines bend as a jet
Notes: Make one by one

## Slide 7: Target Floc Size and Energy Dissipation Rate
Broken Floc size function of Capture Sed Velocity
Energy Dissipation as a function of Floc Size
DFlocMax=0.113mm
εFloc=300 mW/kg
Notes: Add Top Function and target floc size and energy dissipation rate

## Slide 8: Optimal Number of Devices
Time from broken to full floc size
Maximum Possible Devices = 75
Head loss is main constraint
Design Number of Device =5
Notes: What number leads to a feasible solution

## Slide 9: Orifice Size and Porosity – Head Loss

## Slide 10: Head Loss
Notes: Maximum headloss through entire flocculator = 5cm (only 10 cm of freeboard)
With 5 breakup devices we have a minumum of 0.39 porosity
If we increase number of devices, we decrease the headloss per device, which means we need a higher porosity, but we run into trouble with a high porosity because our streamlines don’t form a jet

## Slide 11: What do the streamlines look like?

## Slide 12: Energy Dissipation
  Flow Expansion creates energy dissipation, jets and mixing

## Slide 13: Orifice Size and Porosity Design
Case 1: Orifice Diameter 1 cm; 11,887 orifices
Case 2: Orifice Diameter 5 cm; 475 orifices
Question: Does case 1 have more, less, or the same head loss as case 2? Why?
Notes: Add Tricky Question Slide Porosity

## Slide 14: Orifice Size and Porosity Design
Case 1: Orifice Diameter 9.4 cm; 5 orifices
Case 2: Orifice Diameter 2.6 cm; 100 orifices
Question: Does case 1 have a higher, lower, or the same energy dissipation rate as case 2? Why?
Notes: Add Tricky Question Slide Energy Dissipation Rate

## Slide 15: Final Design
Number of Orifices: 21
Orifice Size: 5.1 cm (2”)
Porosity: 39%
Materials
  Plastic sheets, drill holes
  Foam blocks for support
What’s Next?
  HAVE DREW TEST IT!
Notes: Include Materials Selection and Optimal Placement

## Slide 16: ¿Preguntas?