## Slide 1: Anaerobic Wastewater Treatment
Ge Gao, Maithili Gokarn, Walker Grimshaw, Caitlin Rose McKinley, Liankun Zhu

## Slide 2: Review
Anaerobic Wastewater Treatment
Absence of oxygen
Low cost
Energy Neutral or Energy Positive
Low production of waste biological sludge

## Slide 3: Review
Testing the model developed
Reactor Operation
Three reactors without media ( UASB)
Three reactors with media( AFBR).
Data Collection and Analysis

## Slide 4: Data Analysis –Results from past two weeks
Reactor 2.4 ,2.5 and 2.6. (UASB)
Inoculated on November 22,2013
Reactor 2.1,2.2,2.3 (AFBR)
Inoculated on December 6,2013 –insufficient data to conduct analysis

## Slide 5: Data Analysis –Results from past two weeks
COD Removal
Biogas Production
Methane Production
Sand Fluidization
Dissolved Methane
Microscopy

## Slide 6: Biogas Production
Pressure sensor connected to process controller ,records pressure within gas chamber .
Pressure measured is recorded on Microsoft Excel every 30 seconds .
Pressure is recorded in terms of height of water (cm).

## Slide 7: Biogas Production
Chart: Reactor 2.4 12-6-2013
Graph of the pressure data recorded for Reactor 2.4 on December 6,2013

## Slide 8: Biogas Production
Reactor 2.4 Reactor 2.6
Reactor 2.4 |  |  | 
Date | Pressure(cm) | Cross sectional area of gas chamber(cm2) | Volume of biogas collected(cm3)
11/22/2013 | - | 11.40 | 
11/23/2013 | 4.18 |  | 47.63
11/26/2013 | 4.68 |  | 53.33
11/27/2013 | 16.9 |  | 192.58
11/28/2013 | 11.69 |  | 133.21
11/29/2013 | 5.32 |  | 60.62
11/30/2013 | 20.27 |  | 230.98
12/1/2013 | 2.37 |  | 27.01
12/2/2013 | 20.43 |  | 232.80
12/3/2013 | 25.56 |  | 291.26
12/4/2013 | 29.16 |  | 332.28
12/5/2013 | 38.84 |  | 442.59
12/6/2013 | 42.56 |  | 484.98
12/7/2013 | 15.95 |  | 181.75
12/8/2013 | 21.26 |  | 242.26
12/9/2013 | 13 |  | 148.14
12/10/2013 | 14.75 |  | 168.08
Total volume of biogas collected |  |  | 3269.49
Reactor 2.6 |  |  | 
Date | Pressure (cm) | Cross sectional area of gas chamber(cm2) | Volume of gas collected(cm3)
11/22/2013 | 4.63 | 11.40 | 52.76
11/23/2013 | 1.82 |  | 20.74
11/26/2013 | 4.32 |  | 49.23
11/27/2013 | 18.69 |  | 212.98
11/28/2013 | 12 |  | 136.74
11/29/2013 | 6.67 |  | 76.01
11/30/2013 | 27.92 |  | 318.15
12/1/2013 | 3.58 |  | 40.79
12/2/2013 | 22.05 |  | 251.26
12/3/2013 | 31.93 |  | 363.85
12/4/2013 | 34.7 |  | 395.41
12/5/2013 | 52.04 |  | 593.00
12/6/2013 | 57.41 |  | 654.19
12/7/2013 | 25.77 |  | 293.65
12/8/2013 | 33.91 |  | 386.41
12/9/2013 | 12.11 |  | 138.00
12/10/2013 | 14.42 |  | 164.32
Total volume of biogas collected |  |  | 4147.49

## Slide 9: Biogas Production
Chart: Reactor 2.4 Volume of biogas collected (cm3)
| 41600.0 | 41601.0 | 41604.0 | 41605.0 | 41606.0 | 41607.0 | 41608.0 | 41609.0 | 41610.0 | 41611.0 | 41612.0 | 41613.0 | 41614.0 | 41615.0 | 41616.0 | 41617.0 | 41618.0
Reactor 2.4 Volume of gas collected (cm3) | 47.6317 | 53.3292 | 192.5778 | 133.2092 | 60.6221 | 230.9795 | 27.0065 | 232.8027 | 291.2597 | 332.2822 | 442.5872 | 484.9771 | 181.7525 | 242.2606 | 148.1368 | 168.0783

## Slide 10: Biogas Production
Chart: 
| 41600.0 | 41601.0 | 41604.0 | 41605.0 | 41606.0 | 41607.0 | 41608.0 | 41609.0 | 41610.0 | 41611.0 | 41612.0 | 41613.0 | 41614.0 | 41615.0 | 41616.0 | 41617.0 | 41618.0
Reactor 2.6 Volume of Gas Collected(cm3) | 52.7595 | 20.7392 | 49.227 | 212.9751 | 136.7417 | 76.0056 | 318.1523 | 40.7946 | 251.2628 | 363.8468 | 395.4113 | 593.003 | 654.1949 | 293.6527 | 386.4091 | 137.9951 | 164.3179

## Slide 11: Biogas Production
Reactor 2.5
Not air tight
Clogging of granules
Erratic data and graph
No conclusion from data

## Slide 12: Biogas Production
Chart: 
Graph of the pressure data recorded for Reactor 2.5 on December 6,2013

## Slide 13: Biogas Production
Conclusions
Reactor 2.6 has produced most amount of biogas
Similarity in the graphs of reactor 2.4 and 2.6 could be because they share same influent line .
More data required to reach solid conclusion and understand trend .

## Slide 14: Results from the past two weeks
Methane Production data from UASB reactors (2.4, 2.5, and 2.6)
Inoculated on November 22
Standard Curve for methane
Chart: Methane Standard Curve
| 0.0 | 24.69986732940933 | 46.32242288547761 | 74.92249225948837 | 100.5117137558725
area | 0 | 0.2042 | 0.379 | 0.557 | 0.742

## Slide 15: Methane Production
Chart: Methane Production in R2.4
| 41600.0 | 41600.0 | 41601.0 | 41601.0 | 41604.0 | 41604.0 | 41605.0 | 41608.0 | 41608.0 | 41609.0 | 41609.0 | 41610.0 | 41610.0 | 41611.0 | 41613.0 | 41613.0
 | 0.48733 | 0.49925 | 0.7198 | 0.67884 | 0.50607 | 0.53175 | 0.6176 | 0.60162 | 0.56073 | 0.39574 | 0.40514 | 0.44692 | 0.45402 | 0.59109 | 0.51079 | 0.56058
Chart: Methane Production in R2.5
| 41604.0 | 41604.0 | 41605.0 | 41608.0 | 41608.0 | 41609.0 | 41609.0 | 41610.0 | 41610.0 | 41611.0 | 41613.0 | 41613.0
 | 0.21608 | 0.20423 | 0.59025 | 0.60921 | 0.53471 | 0.40143 | 0.33852 | 0.39213 | 0.39637 | 0.44768 | 0.55606 | 0.58085
Chart: Methane Production R2.6
| 41601.0 | 41601.0 | 41602.0 | 41602.0 | 41603.0 | 41603.0 | 41604.0 | 41604.0 | 41605.0 | 41608.0 | 41608.0 | 41609.0 | 41609.0 | 41610.0 | 41610.0 | 41611.0 | 41611.0 | 41613.0 | 41613.0
 | 0.81917 | 0.82257 | 0.83453 | 0.81461 | 0.7768 | 0.82248 | 0.69556 | 0.71397 | 0.71915 | 0.62595 | 0.581 | 0.53505 | 0.50467 | 0.27663 | 0.3091 | 0.6571 | 0.64782 | 0.29095 | 0.55081

## Slide 16: Methane Production Deliverables
Difficult to classify methane trends, but 2.4 and 2.6 (the most stable reactors) have negative trends
Instabilities may be due to outside influences
  Extraction methods
  Time of day of sampling

## Slide 17: Results from the past two weeks
COD Removal

## Slide 18: Results from the past two weeks
Fluidization Velocity Test 1----0.15 mm Sand

## Slide 19: Results from the past two weeks
Fluidization Velocity Test 2----Quartz Powder
Two inlet geometries

## Slide 20: Results from the past two weeks
Fluidization Velocity Test 2----Quartz Powder
Chart: Upflow Velocity (mm/s)
Chart: Upflow Velocity (mm/s)
| 0.292 | 0.365 | 0.439 | 0.512 | 0.585 | 0.658 | 0.731 | 0.804 | 0.877 | 0.95 | 1.023 | 1.096 | 1.169
Percent Bed Expansion | 0.024 | 0.072 | 0.1 | 0.14 | 0.168 | 0.192 | 0.204 | 0.228 | 0.252 | 0.28 | 0.304 | 0.316 | 0.328
Flow Rate (mL/min) | Upflow Velocity (mm/s) | Percent Bed Expansion (%)
20 | 0.292 | 2.40%
25 | 0.365 | 7.20%
30 | 0.439 | 10%
35 | 0.512 | 14%
40 | 0.585 | 16.80%
45 | 0.658 | 19.20%
50 | 0.731 | 20.40%
55 | 0.804 | 22.80%
60 | 0.877 | 25.20%
65 | 0.95 | 28%
70 | 1.023 | 30.40%
75 | 1.096 | 31.60%
80 | 1.169 | 32.80%

## Slide 21: Results from the past two weeks
Fluidization Velocity Test 2----Quartz Powder
Chart: Upflow Velocity (mm/s)
| 0.292 | 0.365 | 0.439 | 0.512 | 0.585 | 0.658 | 0.731 | 0.804 | 0.877 | 0.95 | 1.023 | 1.096 | 1.169
 | 0.015 | 0.06 | 0.08 | 0.095 | 0.1 | 0.105 | 0.115 | 0.13 | 0.14 | 0.145 | 0.15 | 0.155 | 0.16
Flow Rate (mL/min) | Upflow Velocity (mm/s) | Percent Bed Expansion( %)
20 | 0.292 | 1.50%
25 | 0.365 | 6%
30 | 0.439 | 8%
35 | 0.512 | 9.50%
40 | 0.585 | 10%
45 | 0.658 | 10.50%
50 | 0.731 | 11.50%
55 | 0.804 | 13%
60 | 0.877 | 14%
65 | 0.95 | 14.50%
70 | 1.023 | 15%
75 | 1.096 | 15.50%
80 | 1.169 | 16%

## Slide 22: Results from the past two weeks
Where is the methane going?
  Previous research has indicated high dissolved methane concentrations in effluent…

## Slide 23: Dissolved Methane

## Slide 24: Granule Characterization
Confocal Microscopy - The Biotechnology Resource Center Imaging Facility, Cornell University
  Layered microscopy

## Slide 25: DAPI (DNA stain)

## Slide 26: DAPI (DNA Stain)

## Slide 27: Acradine Orange (Nucleic Acid Stain) and Autofluorescence

## Slide 28: Future Directions
Plans to keep anaerobes alive over the break
Moving to a temperature controlled room in January

## Slide 29: Future Directions
Get Methane from liquid to gas phase
Prevent Clogging in AFBRs
Prevent Granule Breakup in UASBs

## Slide 30: Future Directions
Improve biomass adhesion to support material in AFBRs
  Want to wash out non-adhered biomass
Steady State Operation