## Slide 1: Sand Source and Testing Methods
Rebecca Schneider and Meghan Furton

## Slide 2: Introduction
  Need
    SRSF filter media
      Silica sand characteristics:
        Density
        Color
        Hardness
        Effective size
  Local materials
    Reduced cost
    Independent production
What material characteristic does a sample of sand have?

## Slide 3: Background
  Current sand acquisition
    India:
      Taken from the Barakar river
      Sieved to correct for size
      Access to laboratories
  Importance of simplifying test methods
    Honduras:
      Plans to take sand from local river beds
      Imported from the U.S.
      Testing will be done in apartments
Notes: http://www.youtube.com/watch?v=qWqDurunnK8

## Slide 4: Goals
Short term:
  Produce viable sand from a poorly sieved sample
  Understand the relationship between different sand qualities
  Perfect a test procedure
Long term:
  Enable self-sufficient sand sourcing at water plant construction sites

## Slide 5: Specifications
SRSF specifications:
No sand should be able to slide through the 0.2 mm slots in the PVC pipe
The sand should be hard and not prone to dissolution in acid
The backwash velocity required to expand the filter bed by 30% should be very close to 11 mm/s
The sand bed must not have significant stratification after backwash
AWWA standards:
85% silica
Specific gravity >2.5
Acid Solubility <5%
Visibly free of clay, dust, mica, and organic matter

## Slide 6: Research
American Water Works Association (AWWA)
American Society for Testing and Materials (ASTM)
Field sites
SOURCES
Other Topics
RESULTS
Hardness Testing
Backwash Velocity
Filter media standards
  Acid solubility test
Test procedure
  C127
  E11
Other needs
  Lab access
  Current procedure

## Slide 7: Testing
Acid Solubility Test
Uniformity Coefficient
Effective Size
Hardness
Samples:
Playground Sand, Aquamarium Sand, and Filter Sand
Hardness Number | Material
6 | Orthoclase
7 | Vitreous Silica
8 | Quartz

## Slide 8: Uniformity Coefficient and Effective Size
Preliminary Results:
effective size for all
samples are less than
The required 0.2mm
Problems:
Scale doesn’t reach above 200g
Solutions:
Split up samples and measure it in pieces (not quite as exact)

## Slide 9: Procedure
SAND SAMPLE
About 100g
4
10
Pan
200
20
60
70
40
1) Mass the sand sample and all the sieves
2) Pour the sand into the sieve stack (starting with the lowest sieve No.)
3) Shake the sieve stack for 5 to 10 minutes.
Should stay in continuous motion such that not more than 1% of the sand (by wt) will not pass an individual sieve during an addition minute.
5) Graph the results
4) Mass the sand and sieves and then subtract the weight of the sieves to find the sample mass

## Slide 10: Sample Calculations
Sieve No. | Sieve Size (mm) | Sample Weight (g) Sieve before – sieve with sand sample after | % retained Sample Weight/Total Sample (~100g) | % passing last larger sieve Start at 100 and then use % passing calculation for Sieve No. one less | % passing Percent passing next largest sieve – percent retained on sieve
A | B | C | C/100g | 100 | 100 – (C/100)
D | E | F | F/100g | 100 – (C/100) | (100 – (C/100)) - F/100g
Graph the Sieve Size vs the % passing.
The effective size (D10) is the size in which only 10% of the sample is smaller
The Uniformity Coefficient (D60/D10) is the size in which 60% of the sample is smaller / the size in which 10% of the sample is smaller

## Slide 11: Sample Graph

## Slide 12: Our Data…

## Slide 13: Filter Sand
Chart: Filter Sand Uniformity Coeff
| 4.75 | 2 | 0.85 | 0.42499999999999999 | 0.25 | 0.21199999999999999 | 0
Percent Passing | 100 | 99.9801 | 99.9204 | 0.33831 | 0.1592 | 0.12935 | 0.069652
Effecitve Size = D10 | 
Effecitve Size = | 0.463
Uniformity Coefficient = D60/D10 | 
D10 = | 0.463
D60 = | 0.61
Uniformity Coefficient = | 0.759016393

## Slide 14: Aquarium Sand
Chart: Aquamarium Uniformity Coeff
| 4.75 | 2 | 0.85 | 0.42499999999999999 | 0.25 | 0.21199999999999999 | 0
Percent Passing | 100 | 100 | 100 | 14.29 | 2.32 | 1.62 | 0.28
Effecitve Size = D10 | 
Effecitve Size = | 0.39
Uniformity Coefficient = D60/D10 | 
D10 = | 0.39
D60 = | 0.59
Uniformity Coefficient = | 0.661016949

## Slide 15: Playground Sand
Chart: Playground Sand Uniformity Coeff
| 4.75 | 2 | 0.85 | 0.42499999999999999 | 0.25 | 0.21199999999999999 | 0
Percent Passing | 100 | 99.9623 | 99.9434 | 81.1792 | 21.4528 | 11.1038 | 1.0472
Effecitve Size = D10 | 
Effecitve Size = | 0.195
Uniformity Coefficient = D60/D10 | 
D10 = | 0.195
D60 = | 0.338
Uniformity Coefficient = | 0.576923077

## Slide 16: Uniformity Coefficient
Uniformity Coefficient is not an AWWA or AguaClara restriction
However, can be used to measure
BACKWASH VELOCITY

## Slide 17: Backwash Velocity
Preliminary Results:
Still researching best
approach. Have not
done any testing yet.
Problems:
Need to adapt tests and formulas found to the specific filters being used
Solutions:
Still in process
AguaClara specifications:
    The backwash velocity required to expand the filter bed by 30% should be very close to 11 mm/s
    The sand bed must not have significant stratification after backwash

## Slide 18: Approach 1 – Backwash Velocity
In fluid mechanics, Gn represents the ratio of forces in viscous fluids.
Equation: Gn=gL3ρ2/μ2
Given: 11mm/s
Can determine experimentally
Can determine experimentally
Can look up based on temperature
9.8m/s2

## Slide 19: Approach 1 – Backwash Velocity
Given: 1.3L
Can determine experimentally
Depends on filter

## Slide 20: Approach 2 – Backwash Velocity
Design Flow can be calculated fairly easily
Typical rates
  For media-fixed systems
    HLR ~ 7.57 μm/h to 30.27 μm/h
  Need to find rates that match up with filter being used
Conversion factor
    1 gal/(ft2*day) = 30.2675 μm/h
V(backwash)=HLR(backwash)*A(filter)*∆t(backwash)
Substituting the two above equations:
V(backwash) = Design Flow (gal/day) * ∆t(backwash)

## Slide 21: Acid Solubility
Importance
  Limestone vs Silica
  Loss over time
    Lifetime of filter sand: roughly 10-20 years
Preliminary Results:
Aquarium sand: <<5% acid content
Problems:
unspecific size
Drying time
Meaning of 1:1 HCL solution
Filtration
Unspecific containers
Solutions:
Set standard sample size
Filter paper
Ordered 6N HCl Solution

## Slide 22: Clay and Organic Material Test
Specified in AWWA standards
Unnecessary for SRSF design
  Able to backwash instantaneously
Traditional Backwash
SRSF Backwash

## Slide 23: Porosity Test
Procedure:
  Measure a known quantity of sand in a graduated cylinder
  Pour in water until the water line matches the top of the sand
  Porosity= (volume of water/total volume)*100

## Slide 24: Improvements
Filter paper
Standardized sample size
Prewash
Simplify
Make easily to reproduce in a field setting

## Slide 25: Challenges
New team
Lab equipment
  Availability of chemicals
  Drying time
Vague procedure
  Sample size
  How to filter sand

## Slide 26: Future Work
Research:
  Hardness tests
  SRSF Backwash requirements
  Lab Work:
  Preform the hardness test
  Sort a poorly sieve sample
Communication:
  Keep in touch with field sites
  Refine lab procedure and materials list

## Slide 27: Questions?