## Slide 1: Grit Removal Design
2015 March 16 Symposium
Annie Ding and Mary Millard

## Slide 2: Introduction
The problem: large sand particles clogging the flocculator!
The proposed solution: addition of a grit removing chamber that would actually decrease plant area

## Slide 3: How, you may ask??

## Slide 4: Our Goals
Prevent grit build-up in flocculator
Reduce plant size
Cut cost
Make operation easier

## Slide 5: Defining “Grit”
Diameter that will be settled out at 16 mm/s
  dGritSettle = 0.1338 mm
Density
  ρGrit = 2650 kg/m3 (assuming the same density as silica sand)
Is coagulant consumption a problem?

## Slide 6: Critical Assumptions!
Relaxed maximum EDR
  VcGrit = 16 mm/s
Relaxed minimum collision potential
  ψ = 70 m⅔
Minimum width = human width! (~50 cm)

## Slide 7: Design #1: GRF (Grit Removing Flocculator)
Grit removal (sedimentation) capabilities added to the first channel of the flocculator
Plate settlers in series
Main constraints:
  target collision potential of flocculator
  optimal H/S ratio
  achieving Rapid Mix EDR (1 W/kg)?

## Slide 8: GRF: Top View

## Slide 9: GRF: Side View

## Slide 10: Design #2: GRU in Flocculator
A small, grit-removing sedimentation unit added into the first flocculation channel
Plate settlers in parallel
Like a tiny rough sedimentation tank
How should we remove the settled grit?
Main constraints:
  avoiding grit “roll-up” effect
  achieving desired capture velocity
  feasibility of construction

## Slide 11: GRU in Flocculator: Top View

## Slide 12: GRU in Flocculator: Side View

## Slide 13: Design #3: GRU in Entrance Tank
An elevated, small sedimentation unit added inside the minimized entrance tank
(Note that all of our designs eliminate the need for a full-blown entrance tank. Only a small area needed for CDC and LFOM.)
Main constraints:
  achieving capture velocity
  feasibility of construction
  elevation issues with plant flow?

## Slide 14: GRU in Entrance Tank: Top View

## Slide 15: GRU in Entrance Tank: Side View

## Slide 16: GRU in Entrance Tank: Side View

## Slide 17: GRU in Entrance Tank: Another View

## Slide 18: Future Work
Finish evaluating design for GRF (Design #1)
Design hopper (grit removal) system for GRU in Flocculator (Design #2)
  Sloped floor to accumulate grit will impact the height of plates, which will make the unit longer, which will make the sloped floor higher…
Determine design for GRF in Entrance Tank (Design #3)

## Slide 19: Questions?
Text
Picture/graph/table