Transition Flow Rates

| Description | Upper Constraint | Min Q L/s | Max Q L/s |
| --- | --- | --- | --- |
| Pre-fab plants | Number of pre-fab plants needed, beyond 4.9 L/s, use EStaRs design with sed tanks | 1 | 4.9 |
| 2 EStaRS 1 sed tank with room for more sed tanks (include sed inlet and outlet channels when building) | A bigger sed tank (inlet manifold length of 3.5m) could be used at 7.5 L/s | 5 | <7.5 |
| 2 EStaRS or more 2 sed tanks | The masonry needed for the filter box for OStaRs gets too difficult (too small for a normal sized person to maneuver) below 16 L/s. | 7.5 | 16 |
| 2 or more OStaRS | Due to a 24in LFOM (biggest pipe size in database) | 16< | 150 |
| Multiple treatment trains (multiple chemical dosing, entrance tanks, flocculators) |  | 150 | 1000 |