## Slide 1: Linear Chemical Dose Controller Spring 2013
Andrea Castro, Kent Chan, Saugat Ghimire

## Slide 2: LCDC Purpose
To dose coagulant & chlorine
Location within an AguaClara Plant

## Slide 3: Atima, Honduras Chemical Doser
Lever
Constant Head Tank
Coagulant Stock Tank
Linear Flow Orifice Meter
Dosing Tubes
Flow calibration column

## Slide 4
Minimum Dose
Maximum Dose
Atima, Honduras Chemical Doser

## Slide 5: Design Theory
Major losses (hf) - due to viscous shear on the pipe walls
Minor losses (he) - due to expansions/compressions
LCDC system is designed so that hf >> he, maintaining a linear relationship between
Q and HTotal

## Slide 6: LCDC Assembly Drawing

## Slide 7: Dimensioned Lever Arm

## Slide 8: Dimensioned Dosing Tubes

## Slide 9: Background Music
Notes: http://www.youtube.com/watch?v=BNWpZ-Y_KvU

## Slide 10: LCDC Video

## Slide 11: Previous Design – Fall 2012
Weight
Turnbuckle
Cross-bracing
Drop-tube
Anodization
Label
Scale
Logo

## Slide 12: Spring 2013 Challenges
Build-full-scale prototype
Coating
Manifolds
Constant Head Tank
Retrofits
Specification Sheets
Entrance tank float
Drop tube
Create a presentable laboratory set-up

## Slide 13: Dosing Tube Manifolds
Current Design
Fall 2012 – Not chlorine resistant

## Slide 14: Lab Set-Up

## Slide 15: Lever Arm Labels
Had 2 units fabricated: 1 in English, 1 in Spanish
  Prompted the question – can we make a universal lever arm?
Conclusion: Use periodic table symbols
  Coagulants used (PAC, Alum) are Al based
  Disinfectant = Cl

## Slide 16: Reduced Float Size – Statics
What is the minimum rod size we can use, so that the buoyant force on the ball causes just the right amount of torque to close the valve?

## Slide 17: Adjustable Constant Head Tank

## Slide 18: Powder Coating vs. Anodizing
Powder coating chosen over anodizing
Anodizing | Powder Coating
Lost a significant amount of color after 24 hours of soaking | Can be scratched off since it is a coating, not a chemical reaction

## Slide 19: Drop-Tube Design
Drop tube extended to the length of the sedimentation weir
Enables coagulant to mix with water at the bottom of the free fall length of the drop tube

## Slide 20: Entrance Tank Float Improvements

## Slide 21: Entrance Tank Float Improvements

## Slide 22: Specifications for San Nicolás, Honduras
Test average: 7.17 mL/s and 7.67 mL/s
  Percent error = 6.9% and 0.4%, within goal of <10% error
Parameter | Value
Target plant flow rate | 32 L/s
Coagulant stock concentration | 166.7 g/L
Maximum coagulant dose | 40 mg/L
Dosing tube diameter | 0.3175 centimeters (1/8 inches)
Dosing tube length | 1.308 meters (4.292 feet)
Number of Dosing Tubes | 3 (1 spare)
Maximum coagulant flow rate | 7.7 mL/s

## Slide 23: Production of Doser
2 Options:
  1) Mass production in US to reduce unit cost
  2) Production in host country using specifications or a prototype
Remaining components are readily available
  Any fitting must be resistant to chlorine, such as PVC or PVDF and may need to be purchased in US

## Slide 24: Remaining Tasks
Retrofits to existing plants – not a priority?

## Slide 25: Future Work
Test chlorine and coagulant concurrently

## Slide 26: Questions